## Cover
We have published this workbook in conjuction with the RIIO-2 Re-opener Applications 2024 Draft Determinations. It contains the tables used in the core document and annexes.
Contents | Column1
Publisher | Ofgem - Small and Medium Sized Projects
Version | 0.1
Publication data | 2024-09-04
Filename | RIIO-2 Re-opener Applications 2024 Draft Determinations - Data File
Price Base For Costs | 2018/19
Cover table Licencees
Sector_Group | Network Name | Sector_Group_Short | Sector | Network Short Name
National Grid Electricity Transmission | National Grid Electricity Transmission | ET_NGrid | ET | NGET
Scottish Hydro Electric Transmission | Scottish Hydro Electric Transmission | ET_SSE | ET | SHET
SP Transmission | SP Transmission | ET_SPEN | ET | SPT
National Gas Transmission | National Gas Transmission | GT_NGas | GT | NGT
Electricity North West | Electricity North West | ED_ENWL | ED | ENWL
Northern Powergrid | Northern Powergrid - Northern | ED_NPG | ED | NPGN
Northern Powergrid | Northern Powergrid - Yorkshire | ED_NPG | ED | NPGY
National Grid Electricity Distribution | National Grid Electricity Distribution - West Midlands | ED_NGrid | ED | WMID
National Grid Electricity Distribution | National Grid Electricity Distribution - East Midlands | ED_NGrid | ED | EMID
National Grid Electricity Distribution | National Grid Electricity Distribution - South Wales | ED_NGrid | ED | SWALES
National Grid Electricity Distribution | National Grid Electricity Distribution - South West | ED_NGrid | ED | SWEST
SP Energy Networks | SP Energy Networks - Distribution | ED_SPEN | ED | SPD
SP Energy Networks | SP Energy Networks - Manweb | ED_SPEN | ED | SPMW
Scottish and Southern Energy | SSEN Distribution - Hydro | ED_SSE | ED | SSEH
Scottish and Southern Energy | SSEN Distribution - Southern | ED_SSE | ED | SSES
UK Power Networks | UK Power Networks - East | ED_UKPN | ED | EPN
UK Power Networks | UK Power Networks - London | ED_UKPN | ED | LPN
UK Power Networks | UK Power Networks - South East | ED_UKPN | ED | SPN
Cadent | Cadent - East of England | GD_Cad | GD | EoE
Cadent | Cadent - London | GD_Cad | GD | Lon
Cadent | Cadent - North West | GD_Cad | GD | NW
Cadent | Cadent - West Midlands | GD_Cad | GD | WM
Northern Gas Networks | Northern Gas Networks | GD_NGN | GD | NGN
Scotia Gas Networks | Scotia Gas Networks - Scotland | GD_SGN | GD | Sc
Scotia Gas Networks | Scotia Gas Networks - Southern | GD_SGN | GD | So
Wales & West Utilities | Wales and West Utilities | GD_WWU | GD | WWU

## Applications
Applications subject to this consultation/decision | Mechanism | Opex Escalator/Indirect Scaler
NGET MSIP 2024 | ET Medium Sized Investment Projects (MSIP) | Yes
SPT MSIP 2024 | ET Medium Sized Investment Projects (MSIP) | Yes
SSEN-D Orkney Whole System Uncertainty Mechanism (HOWSUM) 2024 | ED Hebrides and Orkney – (SSEN only) | No
Cadent Diversions and loss of development claims policy re-opener 2023 | GD Diversions and Loss of Development Claims policy Re-opener | No
SGN Diversions and Loss of Development Claims policy Re-opener 2023 | GD Diversions and Loss of Development Claims policy Re-opener | No
WWU Diversions and Loss of Development Claims policy Re-opener 2023 | GD Diversions and Loss of Development Claims policy Re-opener | No
Cadent Multiple Occupancy Buildings Safety Re-opener 2023 | GD MOB - Safety related activities | No
Cadent New Large Load Connections Re-opener 2023 | GD New Large Load Connections Re-opener | No
WWU New Large Load Connections Re-opener 2023 | GD New Large Load Connections Re-opener | No
ENWL Storm Arwen Reopeners 2024 | ED Storm Arwen Re-opener | No
NGED Storm Arwen Reopners 2024 | ED Storm Arwen Re-opener | No
NPg Storm Arwen Reopeners 2024 | ED Storm Arwen Re-opener | No
SPEN-D Storm Arwen Reopeners 2024 | ED Storm Arwen Re-opener | No
SSEN-D Storm Arwen Reopeners 2024 | ED Storm Arwen Re-opener | No
UKPN Storm Arwen Reopeners 2024 | ED Storm Arwen Re-opener | No

## Contents
Sheet | Tab Name | Worksheet Title | Link
1 | Cover | Cover Sheet | Click to go to worksheet
2 | Applications | Applications | Click to go to worksheet
3 | Contents | Contents | Click to go to worksheet
Tables and Figures in Core Document
4 | Table1_Licensees | Table 1: List of licensees subject to this consultation | Click to go to worksheet
5 | Table2_Reopener_Applications | Table 2: Re-opener applications covered by this consultation | Click to go to worksheet
6 | Table3_Summary_of_DDs | Table 3: Summary of these Draft Determinations | Click to go to worksheet
7 | Table4_Decision_Implementation | Table 4: Decision Implementation | Click to go to worksheet
Tables and Figures in ET Annex
8 | TableET1_MSIP_DDs | Table ET 1: Draft Determinations on the ET re-opener submissions in 2024 | Click to go to worksheet
9 | TableET2_MSIP_Projects | Table ET 2 Draft Determinations on the MSIP Projects in 2024 | Click to go to worksheet
10 | TableET3_MSIPs_Submitted | Table ET 3: MSIPs submitted in January 2024 Window | Click to go to worksheet
11 | TableET4_MSIP_Eligibility | Table ET 4: Eligibility of Projects under MSIP | Click to go to worksheet
12 | TableET5_NeedsCase_Optioneering | Table ET 5: Draft Views on needs Case and Optioneering on NGET's 2024 MSIP's | Click to go to worksheet
13 | TableET6_NGET_Summary | Table ET 6: Summary of Proposed Adjustments on NGET's 2024 MSIPs | Click to go to worksheet
14 | TableET7_NeedsCase_Optioneering | Table ET 7: Draft Views on needs Case and Optioneering on SPT's 2024 MSIP's | Click to go to worksheet
15 | TableET8_SPT_Summary | Table ET 8: Summary of Proposed Adjustments on SPT's 2024 MSIPs | Click to go to worksheet
Tables and Figures in ED Annex
16 | TableED1_Summary_of_DDs | Table ED 1: Draft Determinations for the re-openers in ED | Click to go to worksheet
17 | TableED2_HOWSUM_Projects | Table ED 2: Draft Determinations on the Hebrides and Orkney re-opener submissions in 2024 | Click to go to worksheet
18 | TableED3_HOWSUM_Projects | Table ED 3: List of projects submitted under Hebrides and Orkney Re-opener | Click to go to worksheet
19 | TableED4_Arwen_Summary | Table ED 4: Storm Arwen Summary | Click to go to worksheet
20 | TableED5_Overview_Of_SARt | Table ED 5: Overview of SARt | Click to go to worksheet
21 | TableED6_DNO_Summary | Table ED 6: Proposed number of units and cost proposed by each DNO | Click to go to worksheet
22 | TableED7_InterconnectorsSummary | Table ED 7: Summary of Cross-boiundary Interconnectors proposal amendments | Click to go to worksheet
23 | TableED8_Vegetation_Summary | Table ED 8: Vegetation management proposal breakdown | Click to go to worksheet
24 | TableED9_Power_Sources_Summary | Table ED 9: Temporary power sources proposal breakdown | Click to go to worksheet
25 | TableED10_Customercare_Summary | Table ED 10: Customer welfare and care proposal breakdown | Click to go to worksheet
26 | TableED11_Customercare_Projects | Table ED 11: Customer care and welfare proposal breakdown | Click to go to worksheet
27 | TableED12_CAI_Summary | Table ED 12: Closely Associated Indirect Cost Proposal breakdown | Click to go to worksheet
28 | TableED13_ENWL_Summary | Table ED 13: Summary of ENWL's consulation position | Click to go to worksheet
29 | TableED14_ENWL_ProposalFunding | Table ED 14: Summary of ENWL's proposal allowances | Click to go to worksheet
30 | TableED15_SSEN_Summary | Table ED 15: Summary of SSEN's proposal amendments | Click to go to worksheet
31 | TableED16_SSEN_ProposalFunding | Table ED 16: Summary of SSEN's accepted proposal amendments | Click to go to worksheet
32 | TableED17_NPG_Summary | Table ED 17: Summary of NPG's proposal amendments | Click to go to worksheet
33 | TableED18_NPG_ProposalFunding | Table ED 18: Summary of NPg proposal amendments | Click to go to worksheet
34 | TableED19_SPEN_Summary | Table ED 19: Summary of SPEN's proposal amendments | Click to go to worksheet
35 | TableED20_SPEN_ProposalFunding | Table ED 20: Summary of SPEN proposal amendments | Click to go to worksheet
36 | TableED21_NGED_Summary | Table ED 21: Summary of NGEDs proposal amendments | Click to go to worksheet
37 | TableED22_NGED_ProposalFunding | Table ED 22: Summary of NGED proposal adjustments | Click to go to worksheet
38 | TableED23_UKPN_Summary | Table ED 23: Summary of UKPN's proposal amendments | Click to go to worksheet
39 | TableED24_UKPN_ProposalFunding | Table ED 24: Summary of UKPN's proposal amendments | Click to go to worksheet
Tables and Figures in GD Annex
40 | TableGD1_Reopener_Applications | Table GD 1: GD re-opener mechanisms subject to this consultation | Click to go to worksheet
41 | TableGD2_Summary_of_DDs | Table GD 2: Summary of our GD Draft Determinations | Click to go to worksheet
42 | TableGD3_Diversions_Summary | Table GD 3: Applications received and summary of our draft determinations | Click to go to worksheet
43 | TableGD4a_Cadent_Costs | Table GD 4a: Summary of Cadent's request under the Diversions and Loss of Development Claims Policy Re-opener and Ofgem's Draft Determinations | Click to go to worksheet
44 | TableGD4b_SGN_Costs | Table GD 4b: Summary of SGN's request under the Diversions and Loss of Development Claims Policy Re-opener and Ofgem's Draft Determinations | Click to go to worksheet
45 | TableGD4c_WWU_Costs | Table GD 4c: Summary of WWU's request under the Diversions and Loss of Development Claims Policy Re-opener and Ofgem's Draft Determination | Click to go to worksheet
46 | TableGD4d_Diversions_Projects | Table GD 4d: Diversions projects per sector group | Click to go to worksheet
47 | TableGD5a_MOBs_Summary | Table GD 5a: Applications received and summary of our draft determinations | Click to go to worksheet
48 | TableGD5b_MOBs_Projects | Table GD 5b: GD MOBs Projects | Click to go to worksheet
49 | TableGD6a_NNL_Summary | Table GD 6a: Applications received and summary of our draft determinations | Click to go to worksheet
50 | TableGD6b_NNL_Projects | Table GD 6b: Summary of Cadent's request under the New Large Load Connections Re-opener and Ofgem's Draft Determinations | Click to go to worksheet
51 | TableGD6c_WWU_Costs | Table GD 6c: Summary of WWU's request under the New Large Load Connections Re-opener and Ofgem's Draft Determinations | Click to go to worksheet
52 | TableGD6d_NNL_Projects | Table GD 6d: New Large Load projects per sector group | Click to go to worksheet

## Core_Document>>
RIIO-2 Re-openers: 30 January 2024 Draft Determinations - Data File
#VALUE!
Price Base for Costs: 2018/19
The following worksheets contain the tables in the Core Document

## Table1_Licensees
Table 1: List of licensees subject to this consultation
Sector | Company Group | Sector Group | Network | Network Short Name
ET | National Grid | National Grid Electricity Transmission | National Grid Electricity Transmission | NGET
ET | Scottish and Southern Energy | Scottish Hydro Electric Transmission | Scottish Hydro Electric Transmission | SHET
ET | SP Energy Networks | SP Transmission | SP Transmission | SPT
GT | National Gas | National Gas Transmission | National Gas Transmission | NGGT
ED | Electricity North West | Electricity North West | Electricity North West | ENWL
ED | Northern Powergrid | Northern Powergrid | Northern Powergrid - Northern | NPGN
ED | Northern Powergrid | Northern Powergrid | Northern Powergrid - Yorkshire | NPGY
ED | National Grid | National Grid Electricity Distribution | National Grid Electricity Distribution - West Midlands | WMID
ED | National Grid | National Grid Electricity Distribution | National Grid Electricity Distribution - East Midlands | EMID
ED | National Grid | National Grid Electricity Distribution | National Grid Electricity Distribution - South Wales | SWALES
ED | National Grid | National Grid Electricity Distribution | National Grid Electricity Distribution - South West | SWEST
ED | SP Energy Networks | SP Energy Networks | SP Energy Networks - Distribution | SPD
ED | SP Energy Networks | SP Energy Networks | SP Energy Networks - Manweb | SPMW
ED | Scottish and Southern Energy | Scottish and Southern Energy | SSEN Distribution - Hydro | SSEH
ED | SSES | SSES | SSEN Distribution - Southern | SSES
ED | UK Power Networks | UK Power Networks | UK Power Networks - East | EPN
ED | UK Power Networks | UK Power Networks | UK Power Networks - London | LPN
ED | UK Power Networks | UK Power Networks | UK Power Networks - South East | SPN
GD | Cadent | Cadent | Cadent - East of England | EoE
GD | Cadent | Cadent | Cadent - London | Lon
GD | Cadent | Cadent | Cadent - North West | NW
GD | Cadent | Cadent | Cadent - West Midlands | WM
GD | Northern Gas Networks | Northern Gas Networks | Northern Gas Networks | NGN
GD | Scotia Gas Network | Scotia Gas Networks | Scotland Gas Network | Sc
GD | Scotia Gas Network | Scotia Gas Networks | Southern Gas Network | So
GD | Wales & West Utilities | Wales & West Utilities | Wales & West Utilities | WWU

## Table2_Reopener_Applications
Table 2 Re-opener applications covered by this consultation
Sector | Reopener Mechanism | Re-opener Applications No. of companies | Re-opener Applications No. of projects | Re-opener Applications Forecast costs Price Base* | Re-opener Applications £m
ET | ET Medium Sized Investment Projects (MSIP) | 2 | 10 | 2018/19 | 97.06
ED | ED Hebrides and Orkney – (SSEN only) | 1 | 3 | 2020/21 | 46.28
ED | ED Storm Arwen Re-opener | 6 | 154 | 2020/21 | 266.75
GD | GD Diversions and Loss of Development Claims policy Re-opener | 3 | 62 | 2018/19 | 149.174
GD | GD MOB - Safety Related Activies | 1 | 4 | 2018/19 | 38.61
GD | GD New Large Load Connections Re-opener | 2 | 33 | 2018/19 | 28.981
* For ED all costs and allowances in these DDs are in 2020/21 prices, all other sectors' are in 2018/19 prices

## Table3_Summary_of_DDs
Table 3: Summary of these Draft Determinations
Sector | Sector Group | Company Requested Number of Projects | Company Requested Forecast costs £m | Ofgem's DD - Projects Approved* | Ofgem's DD - Projects Not Approved | Ofgem's DD - Cost adjustment £m | Ofgem's DD - Allowances £m
ET | National Grid Electricity Transmission | 8 | 85.24 | 8 | 0 | -29.03 | 56.21
ET | Scottish Hydro Electric Transmission | 0 | 0 | 0 | 0 | 0 | 0
ET | SP Transmission | 2 | 11.815 | 2 | 0 | -0.287 | 11.528
ET | Total | 10 | 97.055 | 10 | 0 | -29.317 | 67.738
GT | National Gas Transmission | 0 | 0 | 0 | 0 | 0 | 0
GT | Total | 0 | 0 | 0 | 0 | 0 | 0
ED | Electricity North West | 6 | 27.5 | 6 | 0 | 0 | 27.5
ED | Northern Powergrid | 25 | 34.79 | 14 | 11 | -14.73 | 20.06
ED | National Grid Electricity Distribution | 61 | 61.38 | 15 | 46 | -43.21 | 18.17
ED | SP Energy Networks | 26 | 75.9 | 6 | 20 | -68.24 | 7.66
ED | Scottish and Southern Energy | 11 | 56.75 | 6 | 5 | -6.22 | 50.53
ED | UK Power Networks | 28 | 56.7 | 8 | 20 | -28.2 | 28.5
ED | Total | 157 | 313.012 | 55 | 102 | -160.592 | 152.42
GD | Cadent | 69 | 148.33 | 55 | 14 | -85.785 | 62.545
GD | Northern Gas Networks | 0 | 0 | 0 | 0 | 0 | 0
GD | Scotia Gas Networks | 4 | 15.41 | 3 | 1 | -3.6 | 11.81
GD | Wales & West Utilities | 26 | 53.025 | 24 | 2 | -0.434 | 52.591
GD | Total | 99 | 216.765 | 82 | 17 | -89.819 | 126.946
* Including partial approval
Price Base Conversion
Rate: | 2018/19 to 2020/21 | 1.0383
Rate: | 2020/21 to 2018/19 | 0.96309
| Company forecast totals | 2018/19 prices | 2020/21 prices
| ET Total | 97.055 | 100.7748
| GT Total | 0 | 0
| ED Total | 290.161 | 301.282
| GD Total | 216.765 | 225.0729
| Total | 603.981 | 627.1298

## Table4_Decision_Implementation
Table 4 Decision Implementation
Sector | Network company | Licence condition /Reopener subject to this consultation | Direction/ licence modification
ET | National Grid Electricity Transmission | SpC: 3.14 Medium Sized Investment Projects Re-opener and Price Control Deliverable (MSIPREt) | Licence modification
ET | SP Transmission | SpC: 3.14 Medium Sized Investment Projects Re-opener and Price Control Deliverable (MSIPREt) | Licence modification
ET | Scottish Hydro Electric Transmission | SpC: 3.14 Large onshore transmission investment Re-opener – Final needs case | N/A
ED | Scottish and Southern Energy | SpC: 3.2 (Hebrides and Orkney Re-opener) Part O | Direction
ED | All DNOs | SpC: 3.2 Uncertain Costs (Storm Arwen Re-opener) Part J | Licence modification
GD | Cadent | SpC: 3.20 Diversions and Loss of Development Claims policy Re-opener (DIVt) | Direction
GD | Scotia Gas Network | SpC: 3.20 Diversions and Loss of Development Claims policy Re-opener (DIVt) | Direction
GD | Wales & West Utilities | SpC: 3.20 Diversions and Loss of Development Claims policy Re-opener (DIVt) | Direction
GD | Cadent | SpC: 3.21 Multiple Occupancy Buildings safety Re-opener (MOBSt) | Direction
GD | Cadent | SpC: 3.22 New Large Load Connections Re-opener (NLLRt) | Direction
GD | Wales & West Utilities | SpC: 3.22 New Large Load Connections Re-opener (NLLRt) | Direction
ET | Cadent | SpC: 3.7 Non-operational IT Capex Re-opener and Price Control Deliverable (NOITREt) | *Licence correction
ET | National Grid Electricity Transmission | SpC: 3.7 Non-operational IT Capex Re-opener and Price Control Deliverable (NOITREt) | *Licence correction

## ET_Annex>>
RIIO-2 Re-openers: 30 January 2024 Draft Determinations - Data File
#VALUE!
Price Base for Costs: 2018/19
The following worksheets contain the tables and figures in the ET Annex

## TableET1_MSIP_DDs
Table ET1: Draft Determinations on the ET re-opener submissions in 2024
Sector Group | Network | Company Requested Number of Projects | Company Requested - Forecast costs £m | Ofgem's DD - Projects Approved* | Ofgem's DD - Projects Not Approved | Ofgem's DD - Cost adjustment £m | Ofgem's DD - Allowances £m
National Grid Electricity Transmission | NGET | 8 | 85.24 | 8 | 0 | -29.03 | 56.21
Scottish Hydro Electric Transmission | SHET | 0 | 0 | 0 | 0 | 0 | 0
SP Transmission | SPT | 2 | 11.815 | 2 | 0 | -0.287 | 11.528

## TableET2_MSIP_Projects
Table ET2 Draft Determinations on the MSIP Projects in 2024
Sector Group | Network | Company Requested Project | Company Requested Forecast costs £m | Ofgem's DD - Cost adjustment £m | Ofgem's DD - Allowances £m
National Grid Electricity Transmission | NGET | NGET MSIP Pathfinder 1 - Stalybridge (stage 2) | 4.967 | 0.135 | 5.102
National Grid Electricity Transmission | NGET | NGET MSIP Pathfinder 2 - Stocksbridge (stage 2) | 5.364 | 0.272 | 5.636
National Grid Electricity Transmission | NGET | NGET MSIP Pathfinder 3 - Bradford West (stage 2) | 4.856 | -0.426 | 4.43
National Grid Electricity Transmission | NGET | NGET Leiston Demand Connection (Stage 2) | 6.584 | -1.502 | 6.118
National Grid Electricity Transmission | NGET | NGET Elland (NPG) | 0.102 | -0.025 | 0.077
National Grid Electricity Transmission | NGET | NGET Willesden 66kV SEPD | 4.81 | -0.579 | 4.231
National Grid Electricity Transmission | NGET | NGET Willesden & Kensal Green Microsoft Data Centre Connection | 1.751 | -0.095 | 1.656
National Grid Electricity Transmission | NGET | NGET Hylton Castle | 56.804 | -27.835 | 28.965
SP Transmission | SPT | SPT Constraint Management - Modification of Anglo-Scottish Operational Tripping Scheme (OTS) | 1.027 | -0.028 | 0.999
SP Transmission | SPT | SPT SPT-RI-237 Enoch Hill Collector Substation and Associated 132kV Circuit (stage 2) | 10.788 | -0.259 | 10.529

## TableET3_MSIPs_Submitted
Table ET3: MSIPs submitted in January 2024 window
Sector Group | Project Name | Project
National Grid Electricity Transmission | NGET MSIP Pathfinder 1 - Stalybridge (stage 2) | To provide new shunt reactors at Stalybridge
National Grid Electricity Transmission | NGET MSIP Pathfinder 2 - Stocksbridge (stage 2) | To provide new shunt reactors at Stocksbridge
National Grid Electricity Transmission | NGET MSIP Pathfinder 3 - Bradford West (stage 2) | To provide new shunt reactors at Bradford West
National Grid Electricity Transmission | NGET Leiston Demand Connection (Stage 2) | To connect a new demand for Sizewell C at Leiston 132kV Substation
National Grid Electricity Transmission | NGET Elland (NPG) Connection | To connect a new Battery Energy Storage Solution of Northern Powergrid (NPG) at Elland Substation
National Grid Electricity Transmission | NGET Willesden 66kV SEPD Connection | To connect Southern Electric Power Distribution (SEPD) via two 66kV connections at Willesden substation
National Grid Electricity Transmission | NGET Willesden & Kensal Green Microsoft Data Centre Connection | To connect Microsoft's new data centre at Kensal Green 400kV and Willesden 400kV and 66kV substation
National Grid Electricity Transmission | NGET Hylton Castle Connection | To conoonect the new International Advanced Manufacturing Park (IAMP) at Hylton Castle substation
SP Transmission | SPT Constraint Management - Modification of Anglo-Scottish Operational Tripping Scheme (OTS) | To extend the OTS in response to an STCP 16-1 planning request received from NGESO in respect of the B6 Constraint Management Pathfinders
SP Transmission | SPT SPT-RI-237 Enoch Hill Collector Substation and Associated 132kV Circuit (stage 2) | To connect contracted wind generation at Enoch Hill Collector substation

## TableET4_MSIP_Eligibility
Table ET4: Eligibility of Projects under MSIP
Sector Group | Project Name | Eligibility under SpC 3.13.6
National Grid Electricity Transmission | NGET MSIP Pathfinder 1 - Stalybridge (stage 2) | A system operability project requested by the System Operator under 3.14.6(f)
National Grid Electricity Transmission | NGET MSIP Pathfinder 2 - Stocksbridge (stage 2) | A system operability project requested by the System Operator under 3.14.6(f)
National Grid Electricity Transmission | NGET MSIP Pathfinder 3 - Bradford West (stage 2) | A system operability project requested by the System Operator under 3.14.6(f)
National Grid Electricity Transmission | NGET Leiston Demand Connection (Stage 2) | A 0MW connection project or substation work under 3.14.6(f)
National Grid Electricity Transmission | NGET Elland (NPG) Connection | A 0MW connection project or substation work under 3.14.6(f)
National Grid Electricity Transmission | NGET Willesden 66kV SEPD Connection | A 0MW connection project or substation work under 3.14.6(f)
National Grid Electricity Transmission | NGET Willesden & Kensal Green Microsoft Data Centre Connection | A 0MW connection project or substation work under 3.14.6(f)
National Grid Electricity Transmission | NGET Hylton Castle Connection | A customer connection project under 3.14.6(b), with £28m variance between the funding from demand volume driver and the estimated direct cost, which is higher than the threshold of £11.84m
SP Transmission | SPT Constraint Management - Modification of Anglo-Scottish Operational Tripping Scheme (OTS) | A system operability project requested by the System Operator under 3.14.6(f)
SP Transmission | SPT SPT-RI-237 Enoch Hill Collector Substation and Associated 132kV Circuit (stage 2) | A generation connection project under 3.14.6(a), with £5.68m variance between the funding from volume driver and the estimated direct cost, which is higher than the threshold of £4.24m

## TableET5_NeedsCase_Optioneering
Table ET5: Draft Views on Needs Case and Optioneering on NGET's 2024 MSIP's
Project Name | Needs Case | Optioneering
NGET MSIP Pathfinder 1 - Stalybridge (stage 2) | Approve | Approve
NGET MSIP Pathfinder 2 - Stocksbridge (stage 2) | Approve | Approve
NGET MSIP Pathfinder 3 - Bradford West (stage 2) | Approve | Approve
NGET Leiston Demand Connection (Stage 2) | Approve | Approve
NGET Elland (NPG) Connection | Approve | Approve
NGET Willesden 66kV SEPD Connection | Approve | Approve
NGET Willesden & Kensal Green Microsoft Data Centre Connection | Approve | Approve
NGET Hylton Castle Connection | Approve | Rejected

## TableET6_NGET_Summary
Table ET6: Summary of Proposed Adjustments on NGET's 2024 MSIPs
Project Name | Funding Request £m | Adjustment - OE £m | Adjustment - Risk £m | Adjustment - Cost before 1 Apr 2021 £m | Adjustment - Sole Use Assets £m | Adjustment - Optioneering £m | Draft Determinations £m
NGET MSIP Pathfinder 1 - Stalybridge (stage 2) | 4.967 | -0.11201 | 0.24636 |  |  |  | 5.102
NGET MSIP Pathfinder 2 - Stocksbridge (stage 2) | 5.364 | -0.024515 | 0.29637 |  |  |  | 5.636
NGET MSIP Pathfinder 3 - Bradford West (stage 2) | 4.856 | -0.60375 | 0.17706 |  |  |  | 4.43
NGET Leiston Demand Connection (Stage 2) | 6.58 | -0.48917 | 0.022437 |  |  |  | 6.12
NGET Elland (NPG) Connection | 0.102 | -0.0223 | -0.00263 |  |  |  | 0.077
NGET Willesden 66kV SEPD Connection | 4.81 | -0.11735 | 0.33199 | -0.79165 |  |  | 4.23
NGET Willesden & Kensal Green Microsoft Data Centre Connection | 1.751 | -0.020701 | -0.074221 |  |  |  | 1.656
NGET Hylton Castle Connection | 56.8 |  |  |  | -20.1 | -7.7386 | 28.97
Total | 85.24 | -1.39 | 1 | -0.79 | -20.1 | -7.74 | 56.21

## TableET7_NeedsCase_Optioneering
Table ET7: Draft Views on needs Case and Optioneering on SPT's 2024 MSIPs
Project Name | Needs Case | Optioneering
SPT Constraint Management - Modification of Anglo-Scottish Operational Tripping Scheme (OTS) | Approve | Approve
SPT SPT-RI-237 Enoch Hill Collector Substation and Associated 132kV Circuit (stage 2) | Approve | Approve

## TableET8_SPT_Summary
Table ET8: Summary of Proposed Adjustments on SPT's 2024 MSIPs
Project Name | Funding Request £m | Adjustment - OE £m | Adjustment - Risk £m | Draft Determinations £m
SPT Constraint Management - Modification of Anglo-Scottish Operational Tripping Scheme (OTS) | 1.0271 | -0.001 | -0.02725 | 0.99885
SPT SPT-RI-237 Enoch Hill Collector Substation and Associated 132kV Circuit (stage 2) | 10.7893 | -0.124 | -0.1366 | 10.5287
Total | 11.8164 | -0.125 | -0.16385 | 11.5276

## ED_Annex>>
RIIO-2 Re-openers: 30 January 2024 Draft Determinations - Data File
#VALUE!
Price Base for Costs: 2018/19
The following worksheets contain the tables and figures in the ED Annex

## TableED1_Summary_of_DDs
Table ED1: Draft Determinations for the re-openers in ED
Sector Group | Network | Company Requested Number of Projects | Company Requested - Forecast costs £m | Ofgem's DD - Projects Approved* | Ofgem's DD - Projects Not Approved | Ofgem's DD - Cost adjustment £m | Ofgem's DD - Allowances £m
Electricity North West | ENWL | 6 | 27.5 | 6 | 0 | 0 | 27.5
Northern Powergrid | NPGN | 14 | 28.61 | 8 | 6 | -10.86 | 17.75
Northern Powergrid | NPGY | 11 | 6.18 | 6 | 5 | -3.87 | 2.31
National Grid Electricity Distribution | WMID | 16 | 16.52 | 5 | 11 | -11.75 | 4.77
National Grid Electricity Distribution | EMID | 15 | 14.4 | 1 | 14 | -12.55 | 1.85
National Grid Electricity Distribution | SWALES | 16 | 10.05 | 5 | 11 | -6.06 | 3.99
National Grid Electricity Distribution | SWEST | 14 | 20.39 | 4 | 10 | -12.82 | 7.57
SP Energy Networks | SPD | 13 | 37.15 | 3 | 10 | -33.52 | 3.63
SP Energy Networks | SPMW | 13 | 38.75 | 3 | 10 | -34.72 | 4.03
Scottish and Southern Energy | SSEH | 8 | 51.01 | 2 | 6 | -3.62 | 47.39
SSES | SSES | 3 | 5.736 | 1 | 2 | -2.596 | 3.14
UK Power Networks | EPN | 8 | 42.3 | 3 | 5 | -18.9 | 23.4
| LPN | 0 | 0 | 0 | 0 | 0 | 0
| SPN | 20 | 14.4 | 5 | 15 | -9.3 | 5.1

## ED_HOWSUM_Section>>
RIIO-2 Re-openers: 30 January 2024 Draft Determinations - Data File
#VALUE!
Price Base for Costs: 2018/19
The following worksheets contain the tables and figures in the Hebrides and Orkney mechanism section of the ED Annex

## TableED2_HOWSUM_Projects
Table ED2: Draft Determinations on the Hebrides and Orkney re-opener submissions in 2024
Sector Group | Network | Company requested Project | Company requested Forecast costs £m | Ofgem's DD Cost adjustment £m | Ofgem's DD Allowances £m
Scottish and Southern Energy | SSEH | SSEN-D Pentland Firth East 3 (PFE3) | 34.67 | 0 | 34.67
Scottish and Southern Energy | SSEH | SSEH South Uist-Eriskay solution | 0.36 | 0 | 0.36
Scottish and Southern Energy | SSEH | SSEH Eriskay-Barra solution | 11.25 | -0.11 | 11.14

## TableED3_HOWSUM_Projects
Table ED 3: List of projects submitted under Hebrides and Orkney Re-opener
Project Name | Brief Description
SSEN-D Pentland Firth East 3 (PFE3) | Replace the faulty PFE2 33kV subsea cable
SSEH South Uist-Eriskay solution | Replace the subsea cable which connects South Uist in the Outer Hebrides to the islands of Eriskay with a land-based 11kV cable along the Eriskay Causeway
SSEH Eriskay-Barra solution | Install an additional 11kV subsea cable to connect the Isle of Barra in the Outer Hebrides
SSEH South Uist-Eriskay solution | Install a new 33kV subsea cable (Dunvegan – Loch Carnon)

## ED_Arwen_Section>>
RIIO-2 Re-openers: 30 January 2024 Draft Determinations - Data File
#VALUE!
Price Base for Costs: 2018/19
The following worksheets contain the tables and figures in the Storm Arwen mechanism section of the ED Annex

## TableED4_Arwen_Summary
Table ED4: ED Storm Arwen Summary
Sector Group | Network | Company Requested Number of Projects | Company Requested - Forecast costs £m | Ofgem's DD - Projects Approved* | Ofgem's DD - Projects Not Approved | Ofgem's DD - Cost adjustment £m | Ofgem's DD - Allowances £m
Electricity North West | ENWL | 6 | 27.5 | 6 | 0 | 0 | 27.5
Northern Powergrid | NPGN | 14 | 28.61 | 8 | 6 | -10.86 | 17.75
| NPGY | 11 | 6.18 | 6 | 5 | -3.87 | 2.31
National Grid Electricity Distribution | WMID | 16 | 16.52 | 5 | 11 | -11.75 | 4.77
| EMID | 15 | 14.4 | 1 | 14 | -12.55 | 1.85
| SWALES | 16 | 10.05 | 5 | 11 | -6.06 | 3.99
| SWEST | 14 | 20.39 | 4 | 10 | -12.82 | 7.57
SP Energy Networks | SPD | 13 | 37.15 | 3 | 10 | -33.52 | 3.63
| SPMW | 13 | 38.75 | 3 | 10 | -34.72 | 4.03
Scottish and Southern Energy | SSEH | 5 | 4.726 | 2 | 3 | -3.506 | 1.22
| SSES | 3 | 5.736 | 1 | 2 | -2.596 | 3.14
UK Power Networks | EPN | 8 | 42.3 | 3 | 5 | -18.9 | 23.4
| LPN | 0 | 0 | 0 | 0 | 0 | 0
| SPN | 20 | 14.4 | 5 | 15 | -9.3 | 5.1

## TableED5_Overview_Of_SARt
TableED5 Overview of SARt
DNO | Number of proposals | Requested funding | Proposed funding
ENWL | 7 | £27.5m | £27.5m
SSEN | 5 | £10.48m | £4.37m
NPG | 26 | £34.79m | 20.06m
SPEN | 13 | £75.9m | £7.66m
NGED | 16 | £61.38m | £18.17m
UKPN | 8 | £56.7m | £28.5m
Total | 75 | £266.75m | £106.26m

## TableED6_DNO_Summary
Table ED6: Proposed number of units and cost proposed by each DNO
DNO | Number of interconnectors proposed | Requested funding
ENWL | 11 | £1.6m
SSEN | 4 | £0.14m
NPG | 8 | £4.38m
SPEN | 20 | £3.3m
NGED | 13 | £0.94m

## TableED7_InterconnectorsSummary
Table ED7: Summary of Cross-boundary Interconnectors proposal amendments
DNO | Requested funding | Accepted Proposed funding
ENWL | £1.6m | £1.57m
SSEN | £0.14m | £0.14m
NPG | £4.4m | £1.14m
SPEN | £3.3m | £2.3m
NGED | £0.9m | £0.89m

## TableED8_Vegetation_Summary
Table ED8: Vegetation management proposal breakdown
DNO | Proposal name | Requested funding
ENWL | ETR132 review | £0m
NGED | Resilience tree cutting on High Voltage (HV) circuits | £6.1m
SPEN | Reflecting ETR132 Updates | £10.5m
SSEN | Restoring Overhead Line Resilience (ROLR) | £2.1m

## TableED9_Power_Sources_Summary
Table ED9: Temporary power sources proposal breakdown
DNO | Proposal name | Requested funding
NPG | Power Packs | £2.7m
NGED | Mobile and suitcase generation | £5.3m
UKPN | Additional generators for vulnerable customers | £6.1m
SPEN | Making greater use of generation | £3.5m

## TableED10_CustomerCare_Summary
Table ED10: Customer welfare and care proposal breakdown
DNO | Proposal name | Requested funding
NPg | Food and provision retainer and call out agreement | £0.67m
NPg | Improved Welfare Packs | £0.54m
SPEN | Increased Customer Welfare Support | £1.0m
SPEN | Warm Customer Communication Hubs | £2.3m
SPEN | Digital Switchover Support for Vulnerable Customers | £13.4m
SPEN | Proactive Support - Medical Equipment Back-Ups | £23.5m
SPEN | Proactive Support Medically Dependent Equipment Hospital Bed | £0.03m

## TableED11_CustomerCare_Projects
Table ED11: Customer care and welfare proposal breakdown
DNO | Proposal name | Requested funding
NGED | Enhancements to telephony servers | £0.41m
SPEN | Increased Contact Centre Ramp Up | £1.9m

## TableED12_CAI_Summary
Table ED12: Closely Associated Indirect Cost Proposal Breakdown
DNO | Proposal name | Requested funding
NPg | Indirect Scalar | £2.93m
NGED | Closely associated indirects | £5.2m
SPEN | Associated Indirects for Initiatives | £3.2m
SSEN | N/A | £0.65m

## TableED13_ENWL_Summary
Table ED13: Summary of ENWL's consultation position
Proposed Activity | Consultation position
Proposal 1: HV network strengthening predictive modelling - Develop asset level predictive modelling of vulnerable circuits to determine the susceptibility, vulnerability and recoverability of the wood poles and overhead lines. | Accept: Recommendation met. We are satisfied that this proposal will result in the strengthening of the network infrastructure, in line with the E3C recommendation E2. It is a proactive and innovative method to identifying assets that are vulnerable to storms, and allows for a targeted upgrades to priority poles.
Proposal 2: Targeted HV undergrounding/strengthening - Strengthen vulnerable lengths of OHL through rebuilding approximately 150km of OHL, or undergrounding approximately 80km of OHL, identified through the predictive modelling programme. | Accept: Recommendation met. We are satisfied that this proposal will result in the strengthening of the network infrastructure, in line with the recommendation E3C recommendation E2. ENWL have provided clear optioneering, considering four different options. Their chosen option uses a whole system approach considering the operational impacts and risk of failure of assets, which is estimated to reduce risk to 20,000 customers.
Proposal 3: Pennine and borders interconnection – Design and installations 11 cross-boundary interconnectors. | Partially Accept: Recommendation met. See the Cross-boundary interconnectors section, 4.28
Proposal 4: Low Voltage (LV) automation enhancements - Installation of 750 LV reclosing facilities to automatically restore LV transient faults in aims to reduce the demand on field staff in storm conditions with continued efforts to restore supply to customers. | Accept: Recommendation met. ENWL have evidenced that these LV automation enhancements are an effective method to restoring supply caused by LV faults during a storm event, reducing customer restoration times and increased safety for field staff, in line with the E3C recommendation R1. In addition, the proposal estimated that over 7,500 customers will benefit and has been assessed as being proportionate and good value to consumers.
Proposal 5: Coniston HV interconnector – Installation of a new interconnector to provide an alternative power supply from Ambleside to Coniston, which can be used when a storm results in loss of supply. | Accept: Recommendation met. We are satisfied that this proposal meets the E3C recommendation E2, by strengthen network infrastructure that is expected to benefit 1,386 customers. The proposal targets a rural and remote area which is often isolated during storm events, reducing restoration times caused by having one main supply as well as difficulties accessing the area due to topography and weather conditions. We consider this project separately to those proposed in chapter 3 as we deem it a well specified undergrounding project that demonstrates clear value for these communities.
Proposal 6: Alston HV interconnector: Installation of a new interconnector to provide a new supply from Little Salkeld to Alston, which can be used when a storm event results in a loss of supply. | Accept: Recommendation met. We are satisfied that this proposal meets the E3C recommendation E2, by strengthening network infrastructure that is expected to benefit 1,373 customers. The proposal targets a rural and remote area which is often isolated during storm events, reducing restoration times caused by having one main supply as well as difficulties accessing the area due to topography and weather conditions. We consider this project separately to those proposed in chapter 3 as we deem it a well specified undergrounding project that demonstrates clear value for these communities.
Proposal 7: ETR132 – Recognition that the ETR132 standard is under review. | Reject: Recommendation not met. Vegetation management section of this document, 4.38

## TableED14_ENWLProposalFunding
Table ED14: Summary of ENWL proposal allowances
Proposed activity we are minded to accept | Requested funding | Proposed funding
Proposal 1: HV network strengthening predictive modelling | £0.8m | £0.8m
Proposal 2: Targeted HV undergrounding/strengthening | £12.6m | £12.6m
Proposal 3: Pennine and borders interconnection | £1.6m | £1.6m
Proposal 4: LV automation enhancements | £5.5m | £5.5m
Proposal 5: Coniston HV interconnector | £3.1m | £3.1m
Proposal 6: Alston HV interconnector | £3.9m | £3.9m
Total overall funding requested by ENWL and proposed Draft Determination funding | £27.5m | £27.5m

## TableED15_SSEN_Summary
Table ED15: Summary of SSEN’s proposal amendments
Proposed Activity | Consultation position
Proposal 1: Restoring OHL Resilience – Additional funding for targeted tree harvesting, identified following Storm Arwen | Reject: Recommendation not met. Vegetation management section of this document, 4.38.
Proposal 2: HV Feeder Monitoring – Installation of 200 HV feeder monitoring devices to improve the visibility of defects on their network and improve response time during storm events. | Accept: Recommendation met. We are satisfied with this proposal from SSEN, it meets the E3C (R1) and Ofgem (6) recommendations, ensuring faults are detected and repaired quicker, reducing restoration time. The deployment of HV Feeder monitoring devices has a clear operation use, allowing for improved operational response to faults during a storm. This proposal will help to accurately find faults and allow field staff to get to these locations quickly, reducing the time spent looking for the fault and reducing customer restoration times. However, the cost breakdown submitted by SSEN shows that a large proportion of the cost are closely associated indirect and therefore have been removed from the proposed accepted funding (see section Closely Associated Indirects (CAI) costs for more details).
Proposal 3: Wood Pole Assessment Tool – Deployment of 346 Smart Hammers and 14 Residrills to field staff to provide a more consistent and accurate measurement of condition data for wood poles and ensuring targeting wood pole replacements are carried out. | Reject: Cost of proposal is not appropriate to the benefit. The Ofgem 2 recommendation relating to improving pole condition reporting have been met, despite the proposed technology being an asset health tool rather than a storm resilience tool. However, when assessing the proposal in line with the SARt Principles, it was assess that that proposed cost of £0.95m is not justified for benefits the tool provided which is noted as being a reduction of pole failures by 10 poles per year, which is disproportionately of low value compared to the cost. We also believe the core benefit of this proposal will be in the management of its wider asset health which is funded through NARM. These are the grounds we are minded to reject this proposal on.
Proposal 4: Satellite Communication System – Deployment of fixed location Low Earth Orbit satellite communication systems | Reject: BAU activity. While we agree that the proposal could help to address the E3C (CM4 and R3) and Ofgem (13) recommendations, communication systems are considered as BAU and should have been submitted through Digital Communications at RIIO-ED2. Storm events in the UK are not a new phenomenon, therefore SSEN should have considered communication during storms as part of their ED2 business plans. With ongoing initiatives being explored by mobile networks operators, Ofcom and Government to further national resilient communications this may duplicate efforts. Taking this into account, we suggest discussing this policy area for developing RIIO-ED3 and therefore we reject SSEN’s proposal.
Proposal 5: Cross DNO Interconnection – Design and installations 4 cross-boundary interconnectors. | Partially Accept: Recommendation met. Cross-boundary interconnectors section of this document, 4.28.

## TableED16_SSEN_ProposalFunding
Table ED16: Summary of SSEN's accepted proposal amendments
Proposed activity we are minded to accept | Requested funding | Proposed funding
Proposal 2: HV Feeder Monitoring | £6.7m | £4.22m
Proposal 5: Cross DNO Interconnection | £0.14m | £0.14m
Total overall funding requested by SSEN and our proposed Draft Determination funding | 16.04 | £4.37m

## TableED17_NPG_Summary
Table ED17: Summary of NPG’s proposal amendments
Proposed Activity | Consultation position
Proposal 1: Invest in mobile command vehicles in RIIO-ED2 – Invest in two 4x4 vehicles to be fitted with technology to allow them to act as remote command offices, located strategically to co-ordinate activities in the impacted community. | Reject: Unclear value to consumers. The proposal aims to address E3C recommendations R1 and CM5. While we agree this proposal could help address the recommendation, there is limited evidence that this initiative is necessary. NPG have not provided enough evidence that this proposal will solve the problems presented. It is likely that multiple command posts would be requested during a storm event, meaning local command posts would still be required. Given this, we do not believe that the proposal is reasonable. Alternatives have not been fully explored and in addition to this, the proposed mobile command vehicles have the capability to be utilised outside of a storm event during BAU for a great proportion of time and therefore it is also considered note a proportionate cost to benefit in terms of storm resilience.
Proposal 2: Invest in Unmanned Arial Vehicles (UAVs) for reconnaissance and damage assessment in RIIO-ED2 – Invest in 50 UAVs to carry out post storm reconnaissance damage assessments. | Reject: BAU Activity. Although we agree that the proposal could help address the E3C recommendations R1 and CM5, there is no needs case beyond the RIIO-ED2 provision. The use of UAVs in storm event was clearly identified prior to Storm Arwen as NPg have an existing fleet of 50 UAVs that they use to carry out post storm reconnaissance damage assessments. NPg did not submit this proposal as part of RIIO-ED2 despite being aware of their ageing fleet. Replacement fleets should be claimed within allowances provided in our RIIO-ED2 Final Determinations and is not suitable for the SARt. We believe that using UAVs in place of field staff could be trialled or implemented using their current fleet without the addition of 50 new UAVs.
Proposal 3, 4, 5, 6, 7, 8, 9 & 10: Generator proposals – A mixed use of generators | Reject: BAU Activity. See the Temporary Power Sources section of this document, 4.49.
Proposal 11: Improve the speed of compensation. Invest in improvements to IT systems to allow quicker and more efficient processing of customer compensation. | Accept: Recommendation met. We agree that the proposal meeting the E3C CP2 recommendation. NPg are upgrading their compensation system in line with the recommendation to ensure customer compensation claims are processed quickly and efficiently.
Proposal 12: Establishing a new electronic payment system. Proposal to allow compensation payments to be made via electronic payment | Reject: Proposal lacks maturity. We agree this proposal has the potential to speed up customer compensation payments in line with the E3C recommendation, thus enacting the updates to the GSOP regulation, to allow for electronic payments. However, the proposal is still at the exploratory stage and thus in line with the SARt principles. We do not deem it reasonable in regard to it’s the maturity.
Proposal 13 & 14: Customer Welfare – Proposals for food and provision retainers and call out agreement and improved welfare pack | Reject: Recommendation not met. See Customer care and welfare section of this document, 4.60.
Proposal 15: Convert open conductor to Ariel Bundled Conductor (ABC) – Replacing open wire LV conductors with covered ABC to provide more mechanical strength, making the conductor less likely to break, as well as removing the risk of flashover faults from branches or debris making contact across phases. | Accept: Recommendation met. The proposal seeks to address E3C E2, R1, R5 and Ofgem1 and 6. We agree that this proposal meets E3C E2 and Ofgem 1 by updating and strengthening the network infrastructure. The proposal takes a targeted approach to identifying areas which are the most vulnerable to LV faults under storm conditions (high altitude LV feeders and costal feeders) and looks to improve the network.
Proposal 16: Install Remotely Indicating Fault Flow Indicator (RIFFI) – NPg propose to install 3 RIFFI units per feeder section (equalling 387 units across the network) which will allow for remote communication, improving fault location and restoration time. | Accept: Recommendation met. The proposal seeks to address E3C E2, R1, R5 and Ofgem1 and 6 recommendations. We agree that this proposal meets E3C R1 and Ofgem 6 recommendations by improving fault location and reducing restoration time. We are satisfied with this proposal from NPG as RIFFI has been identified as effective method to fault response and restoration, through improved fault monitoring and remote communication. NPg have provided clear optioneering and we agree with RIFFI being the preferred option as it is reasonable in cost, provides value to consumer and is beneficial as a standalone project.
Proposal 17: Install pole mounted RC/automation point - NPg propose to install pole mounted (PM) remote controlled (RC) isolation points. The installation of additional automated RC units facilitates enhanced capability to isolate faulty sections of network and faster restoration of supplies to healthy sections of the network | Accept: Recommendation met. The proposal seeks to address E3C E2, R1, R5 and Ofgem1 and 6 recommendations. We agree that this proposal meets E3C R1 and Ofgem 6 recommendations by improving fault location and reducing restoration time. We are satisfied that this proposal meets the needs case. The installation of automated RC units will reduce the restoration time cause by faults on the HV overhead line during a storm, and potentially restore customers without the need to deploy staff to site. NPg have demonstrated clear targeting of feeder which have been identifies at high risk, offering value to consumer, however the number of customers who are expected to benefit has not been provided, therefore determination of whether to cost is reasonable has not been fully assessed.
Proposal 18: Install step-up generator platform - NPg propose to enhance restoration capability by installing permanent generator platforms at the base of a pole on a HV line, which would facilitate fast deployment of a large generator which can supply at HV. | Reject: BAU Activity. The proposal seeks to address E3C recommendation R3 and R5a as well as Ofgem 8 recommendation. We acknowledge that generators are a useful tool to increase recovery time and get customer back on supply. However, as part of the RIIO-ED2 price control they are considered as BAU and therefore, it is with the DNOs power to request these as part of their business plans. In addition, while they have a role to play in a storm events, they also have the potential to be used in planned works or other business as usual activities they should be utilised to their maximum potential. However, we do not agree that the SARt is a suitable funding source as the proportionate benefits provided in the context, is low compared to its potential BAU usage.
Proposal 19: Transformer rationalisation – replace several PM transformers with a GM substation - NPg propose to replace a cluster of small PMTs with a GM transformer. This will enable faster restoration of customers as it will only require one large generator to be deployed as opposed to multiple small | Reject: BAU activity. The proposal seeks to address E3C recommendation E2, R1 and R5 as well as Ofgem 1 and 6 recommendations. While we acknowledge the proposal may address recommendations R1 and Ofgem 6 we have assessed this proposal as being an BAU activity which should be funded by other means such as we do not see SARt as the key driver. We note the proposal may create load capacity rather than upgrade assets due to poor condition.
Proposal 20: Install interconnector at 8 locations | Partially Accept: Recommendation met. See the section of this document, 4.28.
Proposal 21: Replace cross arm Proposal 22: Install additional poles on existing line Proposal 23: Upgrade pole size Proposal 24: Upsize conductor Proposal 25: Underground line For the purpose of this document, we have grouped these proposals together. NPg propose to target all legacy specification bare conductor feeders at a high altitude or close to the coast at LV, which are historically impacted by extreme weather conditions, adhering to modern overhead line design specifications such as ENA TS 43-40. | Accept: Recommendation met. The proposal seeks to address E3C recommendation E2, R1 and R5 as well as Ofgem recommendations 1 and 6. We have assessed the proposals as meeting the recommendations as they will strengthen the network infrastructure and increase the resilience of the assets, particularly those which are geographically vulnerable. These proposals have identified at risk assets due to legacy specifications and aim to achieve modern design standards to ensure assets are resilient against storm conditions, focussing particularly on vulnerable geographical locations.
Proposal 26: Indirect Scalar | Reject: Out of scope for SARt. See the closely associated indirects section of this document, 4.81.

## TableED18_NPG_ProposalFunding
Table ED18: Summary of NPg proposal amendments
Proposed activity we are minded to accept | Requested funding | Proposed funding
Proposal 11: Improving the speed of compensation | £0.03m | £0.03m
Proposal 15: Convert open conductor to ABC | £1.79m | £1.79m
Proposal 16: Install RIFFI | £0.30m | £0.30m
Proposal 17: Install pole mounted RC/automation point | £1.04m | £1.04m
Proposal 20: Proposal 20: Install interconnector at 8 locations | £4.38m | £1.14m
Proposal 21: Replace cross arm | £0.39m | £0.39m
Proposal 22: Install additional poles on existing line | £3.75m | £3.75m
Proposal 23: Upgrade pole size | £0.32m | £0.32m
Proposal 24: Upsize conductor | £2.10m | £2.10m
Proposal 25: Underground line | £9.19m | £9.19m
Total overall funding requested by NPG and proposed Draft Determination funding | 34.79 | £20.06m

## TableED19_SPEN_Summary
Table ED19: Summary of SPEN's proposal amendments
Proposed Activity | Consultation position
Proposal 1: Enhanced HV Pole Storm Resilience: Improve the targeting of poles using enhanced asset risk modelling, to avoid damage and reduce interruptions, also saving time on repairing damaged poles | Reject: BAU Activity. As part of RIIO-ED2, SPEN discounted their option for targeted stand-alone intervention and followed a whole circuit approach. It is unclear why this targeted approach is now considered a priority risk rather than being addressed at RIIO-ED2. SPEN did not submit an EJP as part of this proposal.
Proposal 2: Innovative OHL Smart Solutions: Installation of smart technologies on targeted areas of the OHL network, in particular Perch and LineSight solutions to improve its ability to identify faults. | Accept: Recommendation met. We agree that this proposal meets the E3C R1 recommendation and Ofgem 6 recommendation around identifying and assessing faults quickly for reduced restoration time. We recognise that LineSight is an established solution which has proven to be an effective fault detection solution for overhead lines. It allows for network faults to be quickly identified in storm events, providing operational staff with key information, therefore reducing the time off supply for customers. This proposal is above SPEN’s BAU activities and is a technology they have not previously used, and this would be a new capability for SPEN.
Proposal 3: Interconnection across DNOs | Partially Accept: Recommendation met. See the cross-boundary section of this document, 4.28.
Proposal 4: OHL Digital Twin Storm Modelling: Reduce restoration times by avoiding asset failures through the application of digital technology on their HV OHL network | Accept: Recommendation met. We agree that this proposal meets the E2C R1 recommendation and Ofgem recommendation 6 around identifying and assessing faults quickly for reduced restoration time, through avoiding asset failures. This proposal is a proactive method to modelling predictive scenarios combining network risk with environmental scenarios which can be used to identify solutions to improve overhead network resilience.
Proposal 5: Reflecting ETR 132 Updates | Reject: BAU Activity. See vegetation management section of this document, 4.38.
Proposal 6: New Generation Connection Points: Installation of permanent connection points for generators on the HV overhead network. | Reject: BAU Activity. The proposal seeks to address E3C recommendation E2, R1 and R5 as well as Ofgem recommendations 1 and 6. While we acknowledge the proposal may address recommendations R1 and Ofgem 6 we believe this proposal is not above the expectations of its current work and we consider this a BAU activity. As the proposal will create load capacity rather than upgrade assets due to poor condition we consider the driver for this activity to also be outside SARt.
Proposal 7: Keeping Customers Connected – Power Packs | Reject: BAU Activity. See temporary power source section of this document, 4.49.
Proposal 8: Increased Customer Welfare Support | Reject: Proposal is not linked to a recommendation. See customer care and welfare section of this document, 4.60.
Proposal 9: Digital Switchover Support for Vulnerable Customers | Reject: Proposal is not linked to a recommendation. See customer care and welfare section of this document, 4.60.
Proposal 10, 11 & 12: Customer Care | Reject: Proposal is not linked to a recommendation. See customer care and welfare section of this document, 4.60.
Proposal 13: Indirect | Reject: Out of scope for SARt. See the closely associated indirects (CAI) section of this document, 4.81.

## TableED20_SPEN_ProposalFunding
Table ED20: Summary of SPEN proposal amendments
Proposed activity we are minded to accept | Requested funding | Proposed funding
Proposal 2: Innovative OHL Smart Solutions | £4.6m | £4.6m
Proposal 3: Interconnection across DNOs | £3.3m | £2.3m
Proposal 4: OHL Digital Twin Storm Modelling | £0.7m | £0.7m
Total overall funding requested by SPEN and proposed Draft Determination funding | £75.9m | £7.6m

## TableED21_NGED_Summary
Table ED21: Summary of NGEDs proposal amendments
Proposed Activity | Consultation position
Proposal 1: Undergrounding HV OHL in wooded areas: Undergrounding or diversion of 340km of OHL from wooded areas to remove the risk of tree damage or avoid other damage caused by storms. | Accept: Recommendation met. We agree that this proposal meets the Ofgem 1 recommendation, relating to improving network infrastructure against severe weather events. The undergrounding of HV OHL’s is a direct demonstration of strengthening the network in locations identified as being at risk from the impacts of storm. This activity goes beyond NGED’s BAU activities and will provide an increased level of storm resilience along targeted circuits, reducing the number of customers as risk during a storm event.
Proposal 2: Replacing LV open wire OHL impacted by trees: covert the bare conductors to ABC, which will provide resilience to LV OHL. | Reject: Does not meet the SARt principles. While we agree this proposal meets the Ofgem 1 recommendation, we are proposing to reject based on the SARt principles, we do not believe that this proposal will be beneficial as a stand-alone project and therefore does not provide value to consumers. This proposal alone will not solve the issue of damage caused by vegetation during a storm event, vegetation management plays a role in maintaining the networks effectiveness and should be considered within BAU costs. The proposal’s approach has not considered which circuits would best benefit customers who would likely be impacted during a storm event which should be a priority.
Proposal 3: Resilience tree cutting on HV circuits | Reject: BAU Activity.
Proposal 4 and 8: Fault monitoring and detection Application of Pre-Fix and LineSight detectors for fault location: Pre-Fix aims to identify disturbances on the network caused by potential faults, in order to remove these defective components before they cause a fault. LineSIGHT allows for faster identification of the location of faults and can also identify the type of fault. | Accept: Recommendation met. We have assessed both proposals as meeting the E3C R1 and Ofgem 6 recommendations which relate to identifying and assessing faults quickly for reduced restoration time. The Pre-Fix and LineSight provide fault detection capabilities will help to accurately find faults and allow field staff to get to these locations quickly, reducing the time spent looking for the fault and reducing restoration times. This activity goes beyond NGED’s BAU activities and increased monitoring and restorations capabilities which will reduce restoration times during a storm event.
Proposal 5: Torque tooling for LV fuses: Replacement of fuses that have been overtightened following storm repair. | Reject: Proposal is not linked to a recommendation. While NGED cite a section of the E3C report they have not provided a link to a specific recommendation this proposal aims to address. In addition, there is no evidence that this tool will provide storm resilience benefits, rather it is an asset replacement tool which will provide no operational benefit during a storm. This request is retrospective which is out of scope of the re-opener
Proposal 6: Reducing customers in a protection zone to 1000: Subdividing circuits into smaller zones by installing additional protection devices, to prevent customers upstream of the devices being affected by faults downstream of the devices. | Reject: BAU Activity. While we agree this proposal meets the Ofgem 3 recommendation, we are proposing the reject this project on the basis that it does not go beyond the BAU activities that NGED can deliver under the current RIIO-ED2 Price Control mechanisms.
Proposal 7: Automation of spur protection: Targeted programme to install TripSaver II to replace fuses on spurs that have either more than 150 customers or are longer than 10km, or where both situations apply. | Accept: Recommendation met. We agree that the proposal meets the Ofgem 3 recommendation relating to improving organisational resilience to improve the speed of customer restoration. The automation enhancements have been shown to be an effective method to restoring supply during a storm events and moving the need for operators to go to site to replace fuses, speeding up the restoration of supply, particularly for communities in rural locations that are predominantly supplied from network spurs.
Proposal 9 & 10: Generators | Reject: BAU Activity. See the temporary power sources section of this document,.4.49
Proposal 11: Pre-emptive movement of resources: Funding request to allow for the pre-emptive movement of resources during storm periods to enable staff to start dealing with storm damage as soon as it occurs. | Reject: Proposal lacks maturity. While the proposal meets the E3C R7 recommendation, we do not believe it meets the SARt principles on the basis of the proposal not being mature enough to implement. NGED have provided no evidence on the practicalities of how this proposal will enhance business operation beyond the current process during a storm event. Furthermore, with the additional funding for fault monitoring and detection being funded through the SARt, we expect NGED to have more capability for early detection of faults we expect that they will be able to deploy resources more strategically and efficiently to the areas where they are required during a local storm event. The North East South West Area Consortium (NEWSAC) agreement provides the means for co-ordination of mutual aid between network operators that are able to provide additional support where required. For these reasons we reject this proposal.
Proposal 12: Enhancements to telephony servers | Reject: Does not meet the SARt principles. See the customer communication of this document, 4.71.
Proposal 13: Inter-DNO interconnection | Accept: Recommendation met. See the cross-boundary interconnectors section on of this document, 4.28.
Proposal 14 & 15: Inter and Intra-NGED DNO interconnections: Request funding to inter-NGED DNO interconnections to provide alternative supplies that can be used to restore power when repairs are being completed. | Reject: BAU Activity. This proposal does not go beyond the BAU activities that NGED can deliver under the current RIIO-ED2 Price Control mechanisms. We expect to see more mature proposals and will work with NGED as with other DNOs to understand interconnection ahead of RIIO-ED3.
Proposal 16: Network geospatial mapping: Funding to enhance data capture and visualisation and to provide better identification of where trees are close to overhead lines. This will enable to prioritisation of tree clearance activities as well as other resilience activities. | Reject: BAU Activity. While we agree the proposal may support the delivery of Ofgem’s 1 recommendation, there is no clear justification for why this is being proposed now, rather than at the RIIO-ED2 Price Control. We consider it to be an extension of NGED’s RIIO-ED2 Price Control BAU activities, which they have the ability to deliver as part of the RIIO-ED2 Price Control. In addition, the proposed benefits of this proposal go beyond storm resilience and should therefore be considered in the wider context of the RIIO-ED3 Price Control.
Proposal 17: Closely Associated Indirects (CAIs) | Reject: Out of scope for SARt. See the closely associated indirects section of this document, 4.81.

## TableED22_NGED_ProposalFunding
Table ED22: Summary of NGED proposal adjustments
Proposed activity we are minded to accept | Requested funding | Proposed funding
Proposal 1: Undergrounding HV overhead lines in wooded areas | £6.4m | £6.4m
Proposal 4: Application of Pre-Fix detection for fault location | £5.4m | £5.4m
Proposal 7: Automation of spur protection | £1.8m | £1.8m
Proposal 8: LineSight detectors to identify nested and low conductor faults | £3.6m | £3.6m
Proposal 13: Inter-DNO interconnection | £0.94m | £0.89m
Total overall funding requested by NGED and proposed Draft Determination funding | £61.37m | £18.17m

## TableED23_UKPN_Summary
Table ED23: Summary of UKPN's proposal amendments
Proposed Activity | Consultation position
Proposal 1: Modernisation of the overhead network: Programme to target the replacement of small section overhead line conductor with a more robust conductor. | Accept: Recommendation met. We agree that this proposal meets the E3C E2 recommendation, relating to ensuring network infrastructure is fit for purpose. This proposal uses identified assets which have a higher-than-normal failure rate during abnormal weather conditions such as extreme storms but are typically not identified as poor performers day to day. The aims to achieve modern design standards to ensure assets are resilient against storm conditions. We would like to see UKPN further develop their methodology to demonstrate that the types of faults seen on selected feeders is likely to be mitigated by modernising the OHL, and that the impacts of such faults could not be more economically minimised or mitigated via alternate methods e.g. vegetation management.
Proposal 2: Resilience communications: Installation of BGAN on overhead line secondary sites to provide resilient communications. | Reject: BAU Activity. While we agree that the proposal could help to address the E3C R3 recommendation, communication systems are considered as BAU and should have been submitted through Digital Communications at RIIO-ED2. Storm events in the UK are not a new phenomenon, therefore SSEN should have considered communication during storms as part of their ED2 business plans. With ongoing initiatives being explored by mobile networks operators, Ofcom and Government to further national resilient communications this may duplicate efforts. Taking this into account, we suggest that this policy area is developed ahead of RIIO-ED3 allowing engagement with key stakeholders (e.g. Ofcom). We therefore we reject UKPN’s proposal.
Proposal 3 & 4: Distribution Fault Anticipation (DFA) & Metrysense 5000 sensors: DFA & Metrysense 5000 are complementary programmes. DFA is an innovative solution which allows real time monitoring of the network, meaning an issue can be identified before it causes a permanent interruption. Metrysense technology helps to reduce interruptions and assists in locating downed conductions on HV feeders, ensuring faults not which are not identified via the application of arc suppression coils are located and repaired. | Accept: Recommendation met. We agree that both proposals meet the E3C R1 recommendation relating to quickly identifying and assessing faults in the network in a severe weather event. Both proposals provide fault detection capabilities which will help to accurately find faults. DFA also promotes proactive repair, reducing the likelihood of a fault during an event, while Metrysense 5000 works to identify and locate faults for repair. These proposals reduce the time taken to identify and assess the impacts of faults, allowing for faster more coordinated restorations. This activity goes beyond UKPN’s BAU activities and increased monitoring and restorations capabilities which will reduce restoration times during a storm event.
Proposal 5 & 6: Auto Reclose Technology: Deployment of TDAR functionality at source circuit breakers at Primary substations would improve supply restoration following a transient fault. | Reject: BAU Activity. While we agree that the proposal could help to address the E3C R1 recommendation, relating to quickly identifying and assessing faults in the network in a severe weather event, both proposals are considered as BAU under the RIIO-ED2 Price Control and are incentivised activities under the Interruption Incentive Scheme (IIS), therefore having an impact on IIS delivery. The proposed feeders have not been demonstrated to be in storm prone areas and have therefore been proposed to be rejected.
Proposal 7: Overhead circuit sectionalisation enhancement: Further installation of auto-reclosers and fusesavers to limit the number of customers between remote control points to no more than 300. | Reject: Recommendation not met. We do not agree that the proposal will address the E3C R1 recommendation, relating to quickly identifying and assessing faults in the network in a severe weather event. While we accept the concept in principle, the selection methodology focusses on increasing sectionalisation across OHL networks in general, rather than focusing on storm performance.
Proposal 8: Additional Generators for vulnerable customers | Reject: BAU Activity. See the Temporary Power Sources section of this document, 4.81.

## TableED24_UKPN_ProposalFunding
Table ED24: Summary of UKPN's proposal amendments
Proposed activity we are minded to accept | Requested funding | Proposed funding
Proposal 1: Modernisation of the overhead network | £15.5m | £15.5m
Proposal 3: Distribution Fault Anticipation (DFA) | £8.70m | £8.70m
Proposal 4: Metrysense 5000 sensors | £4.30m | £4.30m
Total overall funding requested by UKPN and proposed Draft Determination funding | £56.7m | £28.5m

## GD_Annex>>
RIIO-2 Re-openers: 30 January 2024 Draft Determinations - Data File
#VALUE!
Price Base for Costs: 2018/19
The following worksheets contain the tables and figures in the GD Annex

## TableGD1_Reopener_Applications
Table GD1: GD re-opener mechanisms subject to this consultation
Reopener Mechanism | Company | Re-opener Applications No. of projects | Re-opener Applications Forcast costs £m
GD Diversions and Loss of Development Claims policy Re-opener | Cadent | 45 | 91.49
GD Diversions and Loss of Development Claims policy Re-opener | Northern Gas Networks | 0 | 0
GD Diversions and Loss of Development Claims policy Re-opener | Scotia Gas Networks | 4 | 15.41
GD Diversions and Loss of Development Claims policy Re-opener | Wales & West Utilities | 13 | 42.274
GD MOB - Safety Related Activies | Cadent | 4 | 38.61
GD MOB - Safety Related Activies | Northern Gas Networks | 0 | 0
GD MOB - Safety Related Activies | Scotia Gas Networks | 0 | 0
GD MOB - Safety Related Activies | Wales & West Utilities | 0 | 0
GD New Large Load Connections Re-opener | Cadent | 20 | 18.23
GD New Large Load Connections Re-opener | Northern Gas Networks | 0 | 0
GD New Large Load Connections Re-opener | Scotia Gas Networks | 0 | 0
GD New Large Load Connections Re-opener | Wales & West Utilities | 13 | 10.751
| Cadent | 0 | 0
0 | Northern Gas Networks | 0 | 0
#REF! | Scotia Gas Networks | 0 | 0
#REF! | Wales & West Utilities | 0 | 0
| Cadent | 0 | 0
0 | Northern Gas Networks | 0 | 0
#REF! | Scotia Gas Networks | 0 | 0
#REF! | Wales & West Utilities | 0 | 0
Total | Cadent | 69 | 148.33
Total | Northern Gas Networks | 0 | 0
Total | Scotia Gas Networks | 4 | 15.41
Total | Wales & West Utilities | 26 | 53.025
Total | All GDNs | 99 | 216.765

## TableGD2_Summary_of_DDs
Table GD2: Summary of our GD Draft Determinations
Sector Group | Network | Company requested Number of Projects | Company requested Forecast costs £m | Ofgem's DD Projects Approved* | Ofgem's DD Projects Not Approved | Ofgem's DD Cost adjustment £m | Ofgem's DD Allowances £m
Cadent | EoE | 34 | 58.063 | 27 | 7 | -32.38 | 25.683
Cadent | Lon | 9 | 19.631 | 7 | 2 | -15.197 | 4.434
Cadent | NW | 18 | 50.735 | 16 | 2 | -21.718 | 29.017
Cadent | WM | 8 | 19.901 | 5 | 3 | -16.49 | 3.411
Northern Gas Networks | NGN | 0 | 0 | 0 | 0 | 0 | 0
Scotia Gas Network | Sc | 4 | 15.41 | 3 | 1 | -3.6 | 11.81
Scotia Gas Network | So | 0 | 0 | 0 | 0 | 0 | 0
Wales & West Utilities | WWU | 26 | 53.025 | 24 | 2 | -0.434 | 52.591

## TableGD3_Diversions_Summary
Table GD3: Applications received and summary of our draft determinations
Sector Group | Network | Compant Requested Number of Projects | Company Requested Forecast costs £m | Ofgem's DD Projects Approved* | Ofgem's DD Projects Not Approved | Ofgem's DD Cost adjustment £m | Ofgem's DD Allowances £m
Cadent | EoE | 22 | 35.183 | 16 | 6 | -16.99 | 18.193
| Lon | 8 | 8.861 | 7 | 1 | -4.427 | 4.434
| NW | 8 | 35.765 | 7 | 1 | -12.188 | 23.577
| WM | 7 | 11.681 | 5 | 2 | -8.27 | 3.411
Northern Gas Networks | NGN | 0 | 0 | 0 | 0 | 0 | 0
Scotia Gas Network | Sc | 4 | 15.41 | 3 | 1 | -3.6 | 11.81
| So | 0 | 0 | 0 | 0 | 0 | 0
Wales & West Utilities | WWU | 13 | 42.274 | 11 | 2 | -0.434 | 41.84

## TableGD4a_Cadent_Costs
Table GD4a: Summary of Cadent's request under the Diversions and Loss of Development Claims Policy Re-opener and Ofgem's Draft Determinations
Project | Trigger | Cadent submitted costs | Ofgem adjustments | Ofgem assessed efficient costs
Named diversion projects | Diversion | 17.5 | -4.38 | 13.12
Encroached mains diversions | Diversion | 22.4 | -16.55 | 5.85
Encroached services | Diversion | 33.3 | -23.91 | 9.39*
Structural removal/legal remediation | Diversion | 0.33 | 9.98 | 10.31
Completed, future and forecasted projects | Loss of development claims | 8.3 | -6.38 | 1.92
Ulverston and Butterwick projects | Environmental | 9.66 | -0.64 | 9.02
Total |  | 91.49 | -41.88 | 49.61
*Adjusted for ongoing efficiencies in line with RIIO-GD2 Final Determinations (FDs).

## TableGD4b_SGN_Costs
Table GD4b: Summary of SGN's request under the Diversions and Loss of Development Claims Policy Re-opener and Ofgem's Draft Determinations
Project | Trigger | SGN submitted costs | Ofgem adjustments | Ofgem assessed efficient costs
Cowdenhill | Diversion | 1.75 | -1.75 | 0
Meadowhill | Environmental | 6.7 | -0.47 | 6.23
Pitcairngreen | Environmental | 2.87 | 0 | 2.87
Below 7bar washouts | Environmental | 4.09 | -1.38 | 2.71
Moorfield | Loss of development claims | 0 | 0 | 0
Total |  | 15.41 | -3.6 | 11.81

## TableGD4c_WWU_Costs
Table GD4c: Summary of WWU's request under the Diversions and Loss of Development Claims Policy Re-opener and Ofgem's Draft Determination
Trigger | WWU submitted costs | WWU RIIO-GD1 reduction* | Ofgem adjustments | Ofgem assessed efficient costs
Diversion | 5.89 | -0.27 | 0 | 5.62
Loss of development claims | 35.79 | -1.89 | -0.43 | 33.47
Environmental | 2.75 | 0 | 0 | 2.75
Total | 44.43 | -2.16 | -0.43 | 41.84
*Projects which spanned RIIO-GD1 and RIIO-GD2: removal of costs that occurred in RIIO-GD1 and are therefore not within the scope of this re-opener submission.

## TableGD4d_Diversions_Projects
Table GD4d: Diversions projects per sector group
Sector Group | Network | Company Requested Project | Company Requested Forecast costs | Ofgem's DD Cost adjustment £m | Ofgem's DD Allowances £m
Cadent | EoE | EoE Encroached Mains | 3.561 | -2.641 | 0.92
Cadent | EoE | EoE Encroached Services (alterations) | 0.849 | -0.621 | 0.228
Cadent | EoE | EoE Earls Barton-Ecton LDC forecast | 0 | 0 | 0
Cadent | EoE | EoE EM TruFrame | 0.788 | -0.228 | 0.56
Cadent | EoE | EoE EM Willington LDC forecast | 0 | 0 | 0
Cadent | EoE | EoE Encroached Services (relays) | 4.288 | -3.072 | 1.216
Cadent | EoE | EoE Stuctural removal/legal remediation forecast | 0 | 3.38 | 3.38
Cadent | EoE | EoE Wigston Bridge MP Diversion | 0.318 | -0.078 | 0.24
Cadent | EoE | EoE River Ouse | 5.33 | -1.342 | 3.988
Cadent | EoE | EoE Little Braxted Claim | 0.359 | 0 | 0.359
Cadent | EoE | EoE Mangreen Claim | 1.311 | 0 | 1.311
Cadent | EoE | EoE EM Blackburn Rd LDC forecast | 0 | 0 | 0
Cadent | EoE | EoE EM Butterwick Riverbed | 1.529 | -0.369 | 1.16
Cadent | EoE | EoE EM Barton Upon Humber Claim | 0.073 | 0 | 0.073
Cadent | EoE | EoE Carsons Drive | 1.44 | -0.36 | 1.08
Cadent | EoE | EoE EM Alrew as LDC Forecast | 2.313 | -2.313 | 0
Cadent | EoE | EoE EM Cavers Wall LDC forecast | 0 | 0 | 0
Cadent | EoE | EoE EM Encroached Services (relays) | 7.904 | -5.655 | 2.249
Cadent | EoE | EoE EM Lea Road | 0.805 | -0.195 | 0.61
Cadent | EoE | EoE EM Encroached Services (alterations) | 0.253 | -0.194 | 0.059
Cadent | EoE | EoE EM Earls Barton LDC Forecast | 0.304 | -0.304 | 0
Cadent | EoE | EoE EM Encroached Mains | 3.758 | -2.998 | 0.76
Cadent | Lon | Lon Chamberlayne Road | 0.449 | -0.139 | 0.31
Cadent | Lon | Lon Cody Road | 2.151 | -0.511 | 1.64
Cadent | Lon | EoE Harmondsworth Quarry LDC forecast | 0 | 0 | 0
Cadent | Lon | Lon Avondale Drive | 0.316 | -0.076 | 0.24
Cadent | Lon | Lon NL Encroached Services (relays) | 0.85 | -0.622 | 0.228
Cadent | Lon | Lon Stuctural removal/legal remediation forecast | 0 | 0.6 | 0.6
Cadent | Lon | Lon NL Encroached Mains | 1.301 | -0.951 | 0.35
Cadent | Lon | Lon NL Encroached Services (alterations) | 3.794 | -2.728 | 1.066
Cadent | NW | NW Encroached Mains | 11.901 | -8.641 | 3.26
Cadent | NW | NW Crewe IP | 5.931 | -1.477 | 4.454
Cadent | NW | NW Encroached Services (relays) | 0.774 | -0.564 | 0.21
Cadent | NW | NW Encroached Services (alternations) | 6.309 | -4.528 | 1.781
Cadent | NW | NW Completed stuctural removals | 0.328 | 0 | 0.328
Cadent | NW | NW Stuctural removal/legal remediation forecast | 0 | 5.68 | 5.68
Cadent | NW | NW Ulverston | 8.129 | -0.265 | 7.864
Cadent | NW | NW Brewers Barn LDC Forecast | 2.393 | -2.393 | 0
Cadent | WM | WM Wellington Claim | 0.179 | 0 | 0.179
Cadent | WM | WM Wellington Phase 2 LDC Forecast | 0.75 | -0.75 | 0
Cadent | WM | WM Encroached Mains | 1.835 | -1.265 | 0.57
Cadent | WM | WM Stuctural removal/legal remediation forecast | 0 | 0.31 | 0.31
Cadent | WM | WM Encroached Services (alterations) | 2.906 | -2.09 | 0.816
Cadent | WM | WM Encroached Services (relays) | 5.421 | -3.885 | 1.536
Cadent | WM | WM Leigh Sinton | 0.59 | -0.59 | 0
Scotia Gas Networks | Sc | Sc Below bar 7 washouts | 4.09 | -1.38 | 2.71
Scotia Gas Networks | Sc | Sc Meadowhill Restoration/Cowdenhill Quarry | 8.45 | -2.22 | 6.23
Scotia Gas Networks | Sc | Sc Pitcairngreen to Huntingtower Diversion Washout | 2.87 | 0 | 2.87
Scotia Gas Networks | Sc | Sc Loss of Dev Claim Moorfield Kilmarnock | 0 | 0 | 0
Wales & West Utilities | WWU | WWU North Cardiff buildover/diversion | 1.834 | -0.004 | 1.83
Wales & West Utilities | WWU | WWU Treherbert to Ystrad Rhondda Railway Line Diversion - Transport for Wales | 1.424 | -0.004 | 1.42
Wales & West Utilities | WWU | WWU Uckington to Gloucester (Norton) | 0.74 | 0 | 0.74
Wales & West Utilities | WWU | WWU Penylan Cardiff | 0.063 | -0.003 | 0.06
Wales & West Utilities | WWU | WWU River Crossing Brook St | 0.718 | 0.002 | 0.72
Wales & West Utilities | WWU | WWU Central Bristol diversion | 0.502 | -0.002 | 0.5
Wales & West Utilities | WWU | WWU Abergavenny Monmouthshire | 0.28 | 0 | 0.28
Wales & West Utilities | WWU | WWU VN010 Maelor to Moat Lane LTS Diversion | 1.754 | -0.004 | 1.75
Wales & West Utilities | WWU | WWU Land south of Afon Llynfi | 0.282 | -0.002 | 0.28
Wales & West Utilities | WWU | WWU Aberdare to Cwmbach Railway Line Diversion - Transport for Wales | 0.78 | 0.01 | 0.79
Wales & West Utilities | WWU | Redacted | 33.47 | 0 | 33.47

## TableGD5a_MOBs_Summary
Table GD5a: Applications received and summary of our draft determinations
Sector Group | Network | Company Requested Number of Projects | Company Requested Forecast costs £m | Ofgem's DD Projects Approved* | Ofgem's DD Projects Not Approved | Ofgem's DD Cost adjustment £m | Ofgem's DD Allowances £m
Cadent | EoE | 1 | 12.33 | 0 | 1 | -12.33 | 0
Cadent | Lon | 1 | 10.77 | 0 | 1 | -10.77 | 0
Cadent | NW | 1 | 7.29 | 0 | 1 | -7.29 | 0
Cadent | WM | 1 | 8.22 | 0 | 1 | -8.22 | 0
Northern Gas Networks | NGN | 0 | 0 | 0 | 0 | 0 | 0
Scotia Gas Network | Sc | 0 | 0 | 0 | 0 | 0 | 0
Scotia Gas Network | So | 0 | 0 | 0 | 0 | 0 | 0
Wales & West Utilities | WWU | 0 | 0 | 0 | 0 | 0 | 0

## TableGD5b_MOBs_Projects
Table GD5b: MOBs safety projects per sector group
Sector Group | Network | Company Requested Project | Company Requested Forecast costs | Ofgem's DD Cost adjustment £m | Ofgem's DD Allowances £m
Cadent | EoE | Cadent Multiple Occcupancy Buildings Safety Re-opener EoE costs | 12.33 | -12.33 | 0
Cadent | Lon | Cadent Multiple Occcupancy Buildings Safety Re-opener Lon costs | 10.77 | -10.77 | 0
Cadent | NW | Cadent Multiple Occcupancy Buildings Safety Re-opener NW costs | 7.29 | -7.29 | 0
Cadent | WM | Cadent Multiple Occcupancy Buildings Safety Re-opener WM costs | 8.22 | -8.22 | 0

## TableGD6a_NNL_Summary
Table GD6a: Applications received and summary of our draft determinations
Sector Group | Network | Company Requested Number of Projects | Company Requested Forecast costs £m | Ofgem's DD Projects Approved* | Ofgem's DD Projects Not Approved | Ofgem's DD Cost adjustment £m | Ofgem's DD Allowances £m
Cadent | EoE | 11 | 10.55 | 11 | 0 | -3.06 | 7.49
Cadent | Lon | 0 | 0 | 0 | 0 | 0 | 0
Cadent | NW | 9 | 7.68 | 9 | 0 | -2.24 | 5.44
Cadent | WM | 0 | 0 | 0 | 0 | 0 | 0
Northern Gas Networks | NGN | 0 | 0 | 0 | 0 | 0 | 0
Scotia Gas Network | Sc | 0 | 0 | 0 | 0 | 0 | 0
Scotia Gas Network | So | 0 | 0 | 0 | 0 | 0 | 0
Wales & West Utilities | WWU | 13 | 10.751 | 13 | 0 | 0 | 10.751

## TableGD6b_Cadent_Costs
Table GD6b: Summary of Cadent's request under the New Large Load Connections Re-opener and Ofgem's Draft Determinations
Cadent network | RIIO-GD2 Delivery Years | Company request | Ofgem adjustments | Ofgem assessed efficient costs
Eastern | Years 1,2 | 7.87 | -2.28 | 5.59
Eastern | Years 3,4,5 | 2.68 | -0.78 | 1.9
North West | Years 1,2 | 5.92 | -1.73 | 4.19
North West | Years 3,4,5 | 1.76 | -0.51 | 1.25
Total |  | 18.23 | -5.3 | 12.93

## TableGD6c_WWU_Costs
Table GD6c: Summary of WWU's request under the New Large Load Connections Re-opener and Ofgem's Draft Determinations
Column1 | WWU submitted costs | Ofgem adjustments | Ofgem assessed efficient costs
Total | 10.75 | 0 | 10.75

## TableGD6d_NNL_Projects
Table GD6d: New Large Load projects per sector group
Sector Group | Network | Company Requested Project | Company Requested Forecast costs | Ofgem's DD Cost adjustment £m | Ofgem's DD Allowances £m
Cadent | EoE | EoE Penniment Lane - EM | 1.36 | -0.25 | 1.11
Cadent | EoE | EoE Orton PRS | 1.38 | -0.71 | 0.67
Cadent | EoE | EoE NSR6840 POSTLEY ROAD, KEMPSTON | 0.22 | -0.02 | 0.2
Cadent | EoE | EoE Rhodesia, High Grounds Roads | 0.96 | -0.26 | 0.7
Cadent | EoE | EoE EAGR220000 NSR 6894 - EAGLE BUSINESS PA | 0.51 | -0.25 | 0.26
Cadent | EoE | EoE EAGR200001 cambridge bio med, CB2 | 0.47 | -0.25 | 0.22
Cadent | EoE | EoE Balby Carr Bank | 2.17 | -0.25 | 1.92
Cadent | EoE | EoE EAGR220018 Peaking Plant. Great Dunmow | 0.05 | -0.02 | 0.03
Cadent | EoE | EoE Stratton Business Park | 0.11 | -0.02 | 0.09
Cadent | EoE | EoE Tangent Business Hub | 0.64 | -0.25 | 0.39
Cadent | EoE | EoE forecasted projects | 2.68 | -0.78 | 1.9
Cadent | NW | NW NWGR225500 - Mottram Moor, Hollingworth (Complete) | 0.77 | -0.22 | 0.55
Cadent | NW | NW NWGR235359 - Aldon STOR, Aldon Road (Moorland Road - Outlet) | 0.25 | -0.21 | 0.04
Cadent | NW | NW NSR8271 Fishwick Street, Rochdale | 0.41 | -0.22 | 0.19
Cadent | NW | NW NSR4616 - ERF Way, Middlewich (Complete) | 0.24 | -0.21 | 0.03
Cadent | NW | NW NWGR235533 - Ashton Old Road, Manchester | 0.81 | -0.21 | 0.6
Cadent | NW | NW forecasted projects | 1.76 | -0.51 | 1.25
Cadent | NW | NW NWGR235402 - Aldon STOR, Copp Lane | 0.38 | -0.21 | 0.17
Cadent | NW | NW NWGR235383 - Sandy Lane, Dukinfield (Complete) | 0.1 | 0 | 0.1
Cadent | NW | NW NWGR235390 - Moss Lane, Blackrod | 2.96 | -0.45 | 2.51
Wales & West Utilities | WWU | WWU Plymouth STOR Power Generation | 1.23 | 0 | 1.23
Wales & West Utilities | WWU | WWU Padeswood Works, Chester Road | 1.421 | -0.011 | 1.41
Wales & West Utilities | WWU | WWU Oxford Road, Thorne Lane, Yeovil | 0.441 | -0.001 | 0.44
Wales & West Utilities | WWU | WWU Timet, Waunarlywdd Power Generation | 0.559 | 0.001 | 0.56
Wales & West Utilities | WWU | WWU Sudbrook Farm Power Generation | 0.918 | 0.002 | 0.92
Wales & West Utilities | WWU | WWU Rassau (Phase 2 Governor&Reinforcement) | 0.41 | 0.001 | 0.411
Wales & West Utilities | WWU | WWU Northwick 1 and 2 , Five Mile lane, morton in the Marsh | 1.329 | 0.001 | 1.33
Wales & West Utilities | WWU | WWU DEC Anglesey, Parc Business Park, Penrhos, Anglesey, LL65 2FD. | 1 | 0 | 1
Wales & West Utilities | WWU | WWU Crewkerne Power Generation Site | 0.798 | 0.002 | 0.8
Wales & West Utilities | WWU | WWU Avonmouth Power Generation and CNG Filling Station | 0.498 | 0.002 | 0.5
Wales & West Utilities | WWU | WWU Miners Road, Llay, Wrexham | 1.558 | 0.002 | 1.56
Wales & West Utilities | WWU | WWU Kings Weston Lane, Avonmouth | 0.259 | 0.001 | 0.26
Wales & West Utilities | WWU | WWU Felindre STOR | 0.33 | 0 | 0.33