## Index
Index for data in newdistper#12000.xls
References the worksheets in this file to the graphs in the 'Report on distribution and transmission performance 1999/2000'
Sheet | data for:
A to N | Dist Companies individual performance (data in figures 3, 6, 7, 8, 11, 12, 13, 14, 15)
O | Pie chart data - part of data for figures 9 & 10
P | Fig 9
Q | Fig 10
Note
This spreadsheet contains corrected data. It replaces the data in the spreadsheet named distper#12000.xls originally placed on the website and which was the
source of data for the graphs in Figures 12 and 13 in the hardcopy of the report. The corrections made are minor and affect only these two graphs in the report.
Figures 12 and 13 remain correct in the hardcopy report with respect to data for that reporting year (i.e. 1999/2000).
If the graphs were to be replotted, the maximum and minimum performance and the ten year average figures may be slightly changed.
Corrections made:
Sheets changed: B, C, D, F, G, H, I, K, L, M, N
Data changed: 'Security: Number of Customer Supply Interruptions per Circuit km' for the years 1990/91 to 1997/98 inclusive
This data is in the fields from B131 to I 136 and the ten year average in L131 to L136
The original error was caused by the incorrect application of a formula across the years covered by the spreadsheet.
This error has now been corrected and the graphs will be updated in the next hardcopy report for the year 2000/2001.
Note that the graphs in the printed report were created as Lotus files.
The Excel package on which this data is held cannot reproduce the formatting of these graphs in all cases.

## A
Eastern | [12 empty] | Year as |  |  |  |  | better than avg |  | Ten year performance
Year: | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg | % Diff | Max | Min | "Exception" |  |  |  | better than last 9 yrs
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 0.14 | 0.12 | 0.12 | 0.17 | 0.42 | 0.63 | 0.6 | 0.38 | 0.22 | 0.33 | 0.313
LV Faults (All) | 4.21 | 4.21 | 3.88 | 4.03 | 3.86 | 3.13 | 5.36 | 4.58 | 4.07 | 3.54 | 4.087 | [8 empty] | 136408.8972
HV faults:U/G, no dam | 1.31 | 0.65 | 0.52 | 0.6 | 0.79 | 0.29 | 0.36 | 0.14 | 0.24 | 0.68 | 0.558
HV faults:U/G, damage | 20.74 | 19.04 | 18.77 | 16.33 | 15.09 | 23.24 | 22.68 | 21.09 | 21.1 | 20.33 | 19.841
HV faults:O/H, no dam | 5.33 | 4.38 | 8.62 | 4.49 | 8.25 | 0.76 | 0.68 | 0.02 | 0.19 | 1.43 | 3.415 |  |  |  |  | CUSTOMER INTERRUPTIONS
HV faults:O/H, damage | 10.05 | 10.18 | 13.17 | 9.66 | 8.98 | 14.48 | 14.64 | 13.54 | 11.87 | 6.47 | 11.304 |  |  |  |  | 2284567.7325
HV faults: All other | 14.06 | 11.92 | 14.98 | 12.82 | 10.29 | 27.24 | 28.19 | 13.12 | 13.29 | 15.45 | 16.136 |  |  |  |  | 2056930.875
HV faults: Total | 51.48 | 46.16 | 56.06 | 43.9 | 43.41 | 66.01 | 66.55 | 47.91 | 46.68 | 44.34 | 51.25 | -13.48% |  |  |  | 2978205.1664 |  |  |  | 1710534.8625
EHV faults | 8.75 | 8.03 | 14.29 | 6.15 | 6.41 | 8.56 | 9.76 | 11.69 | 6.77 | 8.18 | 8.859 | -7.665% |  |  |  | 1846017.6735 |  |  |  | 295680.5531
132kV faults | 6.56 | 4.58 | 18.29 | 2.77 | 8.48 | 4.21 | 6.5 | 8.43 | 1.78 | 8.91 | 7.051 | 26.37% |  |  |  | 2044336.8054 |  |  |  | 235336.2208
Total of (a) | 71 | 62.98 | 92.53 | 56.85 | 62.16 | 81.92 | 88.19 | 72.59 | 59.31 | 65 | 71.253 | -8.776% |  |  |  | 2685336.16
(b) Planned Outages | 4.75 | 4.52 | 3.89 | 2.3 | 2.61 | 2.87 | 1.06 | 1.12 | 1.09 | 1.61 | 2.582 | -37.65% |  |  |  | 2876067.8301 |  |  |  | 86177.5808
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.03 | 0 | 0 | 0 | 0.005 |  |  |  |  | 2401129.0485
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2006602.76 |  |  |  | 166.8815
Total of (a+b+c+d) | 75.75 | 67.5 | 96.41 | 59.15 | 64.77 | 84.8 | 89.27 | 73.71 | 60.4 | 66.61 | 73.837 | -9.788% | 96.41 | 59.15 |  | 2223194.6769 | 81.3806 | 1 | 0 | 2464405.1247
| ¢ - combined with LV mains figure | [8 empty] | 65 | [5 empty] | 2169458.85
2 AVAILABILITY: Minutes Lost per Connected Customer | [19 empty] | 2327896.0986
(a) Distribution
LV service faults | ¢ | ¢ | ¢ | ¢ | ¢ | [5 empty] | 0
LV Faults (All) | 7.04 | 6.47 | 6.21 | 7.84 | 35.5 | 11.77 | 7.88 | 6.69 | 6.35 | 6.4 | 10.215 | [8 empty] | 34093880.235
HV faults:U/G, no dam | 0.99 | 0.5 | 0.37 | 0.43 | 0.63 | 0.18 | 0.39 | 0.14 | 0.18 | 0.45 | 0.426
HV faults:U/G, damage | 17.89 | 17.05 | 18.51 | 15.72 | 15.79 | 23.65 | 22.16 | 23.88 | 19.46 | 15.67 | 18.978
HV faults:O/H, no dam | 4.18 | 3.59 | 7.67 | 4.53 | 8.41 | 0.72 | 0.63 | 0.01 | 0.21 | 0.07 | 3.002 |  |  |  |  | CUSTOMER MINUTES
HV faults:O/H, damage | 9.92 | 9.98 | 14.85 | 11.23 | 12.89 | 15.29 | 14.53 | 14.55 | 10.3 | 6.83 | 12.037 |  |  |  |  | 228004383.6
HV faults:All other | 11.12 | 8.51 | 12.92 | 9.58 | 8.51 | 22.03 | 21.53 | 11.03 | 9.24 | 11.55 | 12.602 |  |  |  |  | 199354693.1
HV faults:Total | 44.11 | 39.63 | 54.33 | 41.49 | 46.24 | 61.87 | 59.24 | 49.62 | 39.4 | 34.57 | 47.05 | -26.52% |  |  |  | 279749258.24 |  |  |  | 157035444.45
EHV faults | 5.73 | 2.98 | 7.32 | 4.87 | 2.71 | 6.52 | 4.9 | 6.38 | 3.25 | 3.31 | 4.797 | -31% |  |  |  | 197678376.06 |  |  |  | 16010606.313
132kV faults | 1.79 | 0.39 | 9.06 | 0.87 | 2.36 | 0.99 | 2.19 | 3.29 | 0.66 | 4.08 | 2.568 | 58.88% |  |  |  | 297449900.48 |  |  |  | 8571031.272
Total of (a) | 58.67 | 49.48 | 76.92 | 55.07 | 86.81 | 81.15 | 74.2 | 65.97 | 49.66 | 48.36 | 64.629 | -25.17% |  |  |  | 268976949.8
(b) Planned Outages | 16.93 | 15.94 | 13.64 | 8.27 | 7.43 | 3.58 | 3.27 | 4.11 | 3.19 | 4.64 | 8.1 | -42.72% |  |  |  | 249589979.61 |  |  |  | 27034794.9
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0.03 | 0 | 0.023 |  |  |  |  | 228320628.15
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 175677407.2 |  |  |  | 76765.467
Total of (a+b+c+d) | 75.6 | 65.42 | 90.56 | 63.34 | 94.24 | 84.94 | 77.47 | 70.09 | 52.88 | 53 | 72.754 | -27.15% | 94.24 | 52.88 |  | 176894337 | 70.7944 | 1 | 0 | 242825860.266
[10 empty] | 48.36 | [5 empty] | 161407738.44
3(i) QUALITY OF SERVICE: Percentage of Interruptions due to Distribution Faults (Total of (a)) Restored within time specified
LV Faults: 3 hours | 73.83% | 77.08% | 75.62% | 71.74% | 82.16% | 68.88% | 75.13% | 73.98% | 71.2% | 68.61% | 73.82% | -7.061%
24 hours | 99.84% | 99.76% | 99.62% | 98.58% | 99.85% | 99.71% | 99.99% | 100% | 100% | 99.96% | 99.73% | 0.2296%
HV faults:U/G n/dmg 3hrs | 99.84% | 99.98% | 99.98% | 99.97% | 99.88% | 99.99% | 99.97% | 99.99% | 99.99% | 99.94% | 99.95% | -0.01301%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV faults:U/G dmg 3hrs | 97.84% | 97.89% | 98.15% | 97.94% | 97.1% | 98.4% | 98.18% | 97.71% | 97.98% | 98.52% | 97.97% | 0.5604%
24 hours | 99.99% | 99.98% | 99.96% | 99.97% | 99.99% | 100% | 100% | 100% | 100% | 100% | 99.99% | 0.011%
HV faults:O/H n/dmg 3hrs | 99.36% | 99.43% | 98.87% | 99.18% | 98.15% | 99.93% | 99.93% | 100% | 99.98% | 99.94% | 99.48% | 0.4654%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV faults:O/H dmg 3hrs | 98.06% | 97.7% | 97.4% | 96.72% | 96.44% | 98.01% | 98.29% | 98.16% | 98.63% | 98.76% | 97.82% | 0.964%
24 hours | 100% | 100% | 99.99% | 99.97% | 100% | 99.97% | 100% | 100% | 100% | 100% | 99.99% | 0.007%
HV faults:Other 3hr | 98.2% | 98.72% | 98.21% | 98.32% | 98.41% | 98.1% | 98.07% | 98.89% | 99.18% | 98.18% | 98.43%
24 hours | 100% | 99.98% | 99.96% | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 99.99%
HV Faults:Total 3 hours | 93.31% | 93.73% | 92.61% | 92.12% | 89.98% | 94.43% | 94.44% | 94.74% | 95.76% | 95.35% | 93.65% | 1.819%
24 hours | 99.98% | 99.96% | 99.91% | 99.93% | 99.98% | 99.97% | 100% | 100% | 100% | 100% | 99.97% | 0.02701%
EHV Faults: 3 hours | 98.62% | 99.99% | 98.99% | 98.64% | 99.93% | 99.67% | 99.75% | 99.79% | 99.93% | 99.99% | 99.53% | 0.4622%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
132kV F'lts: 3 hours | 100% | 100% | 98.22% | 100% | 100% | 100% | 100% | 99.67% | 99.96% | 100% | 99.78% | 0.2155%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
Total Faults:3 hours | 90.85% | 92.6% | 89.22% | 89.41% | 89.43% | 93.13% | 93.05% | 93.13% | 94.18% | 93.83% | 91.88% | 2.119% | 94.18% | 89.22% |  | 2086023.5653
24 hours | 99.98% | 99.95% | 99.9% | 99.84% | 99.97% | 99.96% | 100% | 100% | 100% | 100% | 99.96% | 0.04002% | 100% | 99.84% |  | 2223194.6769
TOTAL not rest in 3 hrs | 9.15% | 7.4% | 10.78% | 10.59% | 10.57% | 6.87% | 6.95% | 6.87% | 5.82% | 6.17% | 8.117% | -23.99% | 10.78% | 5.82% |  |  |  | 1 | 0
TOTAL not rest in 24 hrs | 0.02% | 0.05% | 0.1% | 0.16% | 0.03% | 0.04% | 0% | 0% | 0% | 0% | 0.04% | -100% | 0.16% | 0% |  |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | NIL * | NIL * | NIL * | NIL | NIL | NIL | NIL | NIL | NIL | nil | N\A |  | N\A
- Load Disconnection | NIL * | NIL * | NIL * | NIL | NIL | NIL | NIL | NIL | NIL | nil | N\A |  | N\A
Total | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0
(b) Eastern Elec.
- Voltage Reductions | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N\A |  | N\A
- Load Disconnection | NIL * | NIL * | NIL * | NIL | NIL | NIL | NIL | NIL | NIL | nil | N\A |  | N\A
Total | N/A | N/A | 0.028 | 0 | 0 | 0 | 0 | 0 | 0
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 1.79 | 1.62 | 1.35 | 1.05 | 1.46 | 0.88 | 0.99 | 1.29 | 1.92 | 1.37 | 1.372 | 10 | 1.92 | 0.88 |  |  |  | 1 | 0
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
| 12.19 | 11.75 | 13.01 | 10.32 | 11.2 | 10.91 | 11.2 | 10.68 | 10.85 | 11.15 | 11.326 |  | 13.01 | 10.32 |  |  |  | 1 | 0
RELEVANT DATA: | N\A: av'ge |  | 10yr av
Number of Customers | 3015931 | 3047305 | 3089104 | 3120909 | 3156302 | 3166670 | 3221763 | 3257535 | 3322190 | 3337629 |  |  | 106%
Embedded Gen.Stations | 0 | N/A | 1 | 4 | 4 | 4 | 4 | 4 | 52 | 53 | N\A
Emb.Gen.Capacity MWSO | 0 | N/A | 140 | 570 | 570 | 570 | 570 | 570 | 509 | 537 | N\A
Mains in commission (circuit kilometres)
Overhead Line | [11 empty] | SUM ALL PESs
132kV | 2309 | 2316 | 2322 | 2330 | 2330 | 2340 | 2341 | 2341 | 2365 | 2365 | 2335.9 | 15049.1 | 101.2% |  | 19085.2
[12 empty] | 4036.1 |  |  | 206071.7
33kV | 3758 | 3777 | 3818 | 3838 | 3838 | 3875 | 3884 | 3884 | 3883 | 3883 | 3843.8 | 28766.8 | 101% |  | 69502.6
25kV | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0.3 | 1812 |  |  | 0
22920
11kV | 19244 | 19542 | 19559 | 19688 | 19832 | 19696 | 19747 | 19547 | 19377 | 19352 | 19558.4 | 139204.3 | 98.94%
6.6kV | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0.6 | 1045 | 0%
3.3kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12323.6
3kV | 2 | 0 | 6 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0%
0
LV | 9592 | 9658 | 9649 | 9640 | 9636 | 9627 | 9619 | 9610 | 9533 | 9515 | 9607.9 | 69502.6 | 99.03%
TOTAL | 34907 | 35294 | 35355 | 35505 | 35643 | 35538 | 35591 | 35382 | 35158 | 35116 | 35348.9 |  | 99.34%
0
Underground Cable | N\A: 0
132kV | 217 | 216 | 216 | 218 | 219 | 219 | 220 | 220 | 220 | 221 | 218.6 | 2724 | 101.1% |  | 5393.7 | 24478.9
[12 empty] | 2669.7 |  |  | 168754.4 | 374826.1
33kV | 2377 | 2361 | 2363 | 2368 | 2371 | 2390 | 2405 | 2436 | 2450 | 2486 | 2400.7 | 14509.5 | 103.6% |  | 306031.3 | 375533.9
25kV | 19 | 19 | 19 | 21 | 22 | 22 | 23 | 23 | 23 | 27 | 21.8 | 42 | 123.9% |  | 0 | 0
[12 empty] | 17601 |  |  | 774838.9
11kV | 14784 | 15017 | 15177 | 15345 | 15470 | 15650 | 15878 | 16317 | 16625 | 16783 | 15704.6 | 116466.8 | 106.9%
6.6kV | 110 | 83 | 82 | 82 | 71 | 75 | 29 | 29 | 29 | 29 | 61.9 | 10538 | 46.85%
3.3kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569.1
3kV | 41 | 18 | 33 | 33 | 30 | 25 | 21 | 21 | 21 | 21 | 26.4 | 21 | 79.55%
9007
LV | 32381 | 32761 | 33233 | 33640 | 33822 | 34120 | 34519 | 34875 | 35221 | 35601 | 34017.3 | 306031.3 | 104.7%
TOTAL | 49929 | 50475 | 51123 | 51707 | 52005 | 52501 | 53095 | 53921 | 54589 | 55168 | 52451.3
Total System length | 84836 | 85769 | 86478 | 87212 | 87648 | 88039 | 88686 | 89303 | 89747 | 90284 | 87800.2 |  | 102.8%
Transformers
Primary Voltage
132kV |  | 219 | 225 | 229 | 228 | 228 | 229 | 229 | 230 | 233
33kV |  | 871 | 853 | 858 | 857 | 850 | 848 | 871 | 869 | 872
Distribution pole-mounted |  | 34051 | 33942 | 34232 | 34256 | 34517 | 34571 | 34579 | 34502 | 34479
Distribution Other |  | 26845 | 25828 | 25871 | 25905 | 26254 | 26416 | 26661 | 26904 | 27230
Capacity |  | 61986 | 60848 | 61190 | 61246 | 61849 | 62064 | 62340 | 62505 | 62814
132kV |  | 12683 | 12683 | 12872 | 12975 | 13228 | 13288 | 13288 | 13306 | 13392
33kV |  | 10316 | 10242 | 10467 | 10535 | 10104 | 10164 | 10392 | 10360 | 10383
Distribution |  | 14956 | 15206 | 14110 | 14149 | 14421 | 14504 | 14615 | 14719 | 14868
|  | 37955 | 38131 | 37449 | 37659 | 37753 | 37956 | 38295 | 38385 | 38643
Network ratios
km 11kV O/H/PMT | NIL: 0.57896; NIL: 0.57062; NIL: 0.5712; NIL: 0.56529; NIL: 0.56162; nil: 0.56127
km 11kV U/G/GMT | NIL: 0.59992; NIL: 0.59896; NIL: 0.60217; NIL: 0.61311; NIL: 0.61902; nil: 0.61741
cust/(PMT+GMT) | NIL: 52.4643; NIL: 52.1082; NIL: 52.827; NIL: 53.1929; NIL: 54.102; nil: 54.0866
HV O/H length (km) | 19248 | 19543 | 19566 | 19695 | 19839 | 19696 | 19747 | 19547 | 19377 | 19352
HV U/G length (km) | 14935 | 15118 | 15292 | 15460 | 15571 | 15750 | 15928 | 16367 | 16675 | 16833
SECURITY : customer supply interruptions per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 2.6454 | 1.3102 | 1.0504 | 1.2112 | 1.6014 | 0.58307 | 0.72817 | 0.27864 | 0.47816 | 1.3483 | 1.1235 |  | 2.6454 | 0.27864
HV faults: U/G damage | 41.8818 | 38.3785 | 37.9169 | 32.9654 | 30.588 | 46.726 | 45.8749 | 41.9756 | 42.0379 | 40.3101 | 39.8655 |  | 46.726 | 30.588
HV faults: O/H no damage | 10.7632 | 8.8287 | 17.4131 | 9.064 | 16.7231 | 1.528 | 1.3754 | 0.039806 | 0.32576 | 2.4663 | 6.8527 |  | 17.4131 | 0.039806
HV faults: O/H damage | 20.2947 | 20.5196 | 26.6044 | 19.5006 | 18.2028 | 29.1133 | 29.6124 | 26.9488 | 20.3511 | 11.1588 | 22.2306 |  | 29.6124 | 11.1588
Security - HV underground networks | 44.5271 | 39.6887 | 38.9673 | 34.1766 | 32.1894 | 47.309 | 46.6031 | 42.2542 | 42.5161 | 41.6584 | 40.989 |  | 47.309 | 32.1894 |  |  |  | 0 | 0
Security - HV overhead networks | 31.0579 | 29.3483 | 44.0175 | 28.5646 | 34.9259 | 30.6413 | 30.9878 | 26.9886 | 20.6769 | 13.6251 | 29.0834 |  | 44.0175 | 13.6251 |  |  |  | 1 | 1
customer supply interruptions per circuit km
Availability : customer minutes lost per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 199.9178 | 100.784 | 74.7429 | 86.8041 | 127.7034 | 36.1905 | 78.8855 | 27.8643 | 35.8617 | 89.2255 | 85.798 |  | 199.9178 | 27.8643
HV faults: U/G damage | 3612.6552 | 3436.7344 | 3739.1653 | 3173.3952 | 3200.6941 | 4755.0315 | 4482.3122 | 4752.8524 | 3877.0505 | 3107.0306 | 3813.6921 |  | 4755.0315 | 3107.0306
HV faults: O/H no damage | 654.9559 | 559.7823 | 1210.949 | 717.8328 | 1337.9959 | 115.7597 | 102.7858 | 1.6665 | 36.0045 | 12.0729 | 474.9805 |  | 1337.9959 | 1.6665
HV faults: O/H damage | 1554.3452 | 1556.1635 | 2344.5362 | 1779.5282 | 2050.7451 | 2458.2851 | 2370.5989 | 2424.7779 | 1765.9368 | 1177.9664 | 1948.2883 |  | 2458.2851 | 1177.9664
Availability - HV underground networks | 3812.573 | 3537.5184 | 3813.9082 | 3260.1992 | 3328.3976 | 4791.222 | 4561.1976 | 4780.7167 | 3912.9122 | 3196.2561 | 3899.4901 |  | 4791.222 | 3196.2561 |  |  |  | 1 | 1
Availability - HV overhead networks | 2209.3011 | 2115.9458 | 3555.4851 | 2497.361 | 3388.741 | 2574.0448 | 2473.3847 | 2426.4444 | 1801.9413 | 1190.0393 | 2423.2689 |  | 3555.4851 | 1190.0393 |  |  |  | 1 | 1
thousands of customer minutes lost per circuit km
| 99/2000: 10066.666 | #mains faults
| 99/2000: 9445.5527 | #faults restd within 3 hrs
103330.9668
86565.495
| 99/2000: 83.77% | %age of all faults restored within 3 hrs
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
| 2284567.7325 | 2056930.875 | 2978205.1664 | 1846017.6735 | 2044336.8054 | 2685336.16 | 2876067.8301 | 2401129.0485 | 2006602.76 | 2223194.6769
| 228004383.6 | 199354693.1 | 279749258.24 | 197678376.06 | 297449900.48 | 268976949.8 | 249589979.61 | 228320628.15 | 175677407.2 | 176894337

## B
East Midlands
Year: | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 1.2 | 1.27 | 1.7 | 1.77 | 2.14 | 2.26 | 2.14 | 1.56 | 1.36 | 0.87 | 1.627
LV faults | 6.5 | 5.92 | 6.56 | 8.3 | 9.25 | 7.95 | 6.98 | 6.44 | 6.32 | 6.44 | 7.066 | [8 empty] | 235836.8651
HV faults: U/G no damage | 0.35 | 0.65 | 0.96 | 1.51 | 1.26 | 1.2 | 3.34 | 3.81 | 4.81 | 5.47 | 2.336
HV faults: U/G damage | 22.47 | 24.08 | 23.3 | 25.4 | 27.8 | 26.15 | 22.59 | 28.12 | 26.86 | 22.72 | 24.949
HV faults: O/H no damage | 5.62 | 5.47 | 7.69 | 7.86 | 10.9 | 9.5 | 11.09 | 10.7 | 6.67 | 8.55 | 8.405
HV faults: O/H damage | 26.5 | 11.15 | 10.93 | 13.79 | 14.64 | 14.13 | 12.07 | 11.37 | 9.08 | 8.92 | 13.258 |  |  |  |  | 3557400
HV faults: All other | 14.66 | 10.65 | 10.86 | 13.65 | 12.47 | 10.55 | 13.48 | 10.41 | 10.35 | 11.75 | 11.883 |  |  |  |  | 1719270
HV faults: Total | 69.6 | 52 | 53.74 | 62.21 | 67.07 | 61.53 | 62.57 | 64.41 | 57.76 | 57.42 | 60.831 | -5.607% |  |  |  | 1639880 |  |  |  | 1459944
EHV faults | 18.8 | 5.71 | 4.56 | 8.5 | 11.22 | 7.32 | 9.86 | 12.42 | 6.18 | 8.39 | 9.296 | -9.746% |  |  |  | 2018500 |  |  |  | 223104
132kV faults | 56.43 | 5.47 | 1.13 | 5.36 | 1.59 | 12.32 | 7.39 | 3.69 | 0.87 | 1.88 | 9.613 | -80.44% |  |  |  | 2113980 |  |  |  | 230712
Total of (a) | 152.55 | 70.36 | 67.69 | 86.14 | 91.28 | 91.39 | 88.95 | 88.53 | 72.5 | 75 | 88.439 | -15.2% |  |  |  | 2234680
(b) Planned Outages | 9 | 9.21 | 6.85 | 5.62 | 4.82 | 5.75 | 4.58 | 4.58 | 3.97 | 2.8 | 5.718 | -51.03% |  |  |  | 2186610 |  |  |  | 137232
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0.002 |  |  |  |  | 2141300
(d) Other Systems | 7.8 | 2.3 | 0 | 0 | 0 | 0 | 1.55 | 0 | 0 | 0 | 1.165 |  |  |  |  | 1758810 |  |  |  | 28008
Total of (a+b+c+d) | 169.4 | 81.87 | 74.54 | 91.75 | 96.09 | 97.16 | 95.07 | 93.1 | 76.47 | 77.8 | 95.325 | -18.38% | 169.4 | 74.54 |  | 1867200 | 81.3806 | 1 | 0 | 2287800
[10 empty] | 75 | [5 empty] | 1800000
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | 4.9 | 1.34 | 2.41 | 3.11 | 4.35 | 3.65 | 2.69 | 2.21 | 1.96 | 1.48 | 2.81
LV faults | 73.95 | 8.52 | 11.52 | 15.02 | 18.26 | 14.8 | 11.21 | 12.27 | 12 | 12.17 | 18.972 | [8 empty] | 63321497.388
HV faults: U/G no damage | 0.24 | 0.47 | 0.63 | 1.2 | 0.82 | 0.62 | 2.47 | 2.35 | 2.89 | 3.73 | 1.542
HV faults: U/G damage | 18.01 | 19.79 | 20.75 | 23.89 | 25.86 | 23.18 | 19.21 | 22.39 | 21.17 | 19.73 | 21.398
HV faults: O/H no damage | 27.44 | 5.02 | 5.38 | 5.2 | 8.73 | 7.52 | 7.04 | 7.34 | 3.78 | 5.98 | 8.343
HV faults: O/H damage | 268.84 | 11.63 | 13.16 | 14.94 | 16.65 | 16.28 | 12.11 | 12.09 | 9.03 | 10.92 | 38.565 |  |  |  |  | 2108148000
HV faults: All other | 14.27 | 6.9 | 9.48 | 9.3 | 11.19 | 7.18 | 7.43 | 6.38 | 6.73 | 7.71 | 8.657 |  |  |  |  | 183414000
HV faults: Total | 328.84 | 43.81 | 49.4 | 54.52 | 63.26 | 54.79 | 48.26 | 50.55 | 43.59 | 48.08 | 78.51 | -38.76% |  |  |  | 191114000 |  |  |  | 262037252.79
EHV faults | 149.08 | 1.86 | 2.4 | 3.65 | 4.39 | 2.81 | 2.96 | 3.86 | 1.48 | 2.45 | 17.494 | -86% |  |  |  | 214280000 |  |  |  | 58388481.726
132kV faults | 418.36 | 0.48 | 0.01 | 4.11 | 0.66 | 2.59 | 0.98 | 0.84 | 0.11 | 0.12 | 42.826 | -99.72% |  |  |  | 230846000 |  |  |  | 142937299.554
Total of (a) | 975.13 | 56.02 | 65.73 | 80.4 | 90.92 | 78.64 | 66.09 | 69.73 | 59.13 | 64.3 | 160.609 | -59.96% |  |  |  | 217557000
(b) Planned Outages | 27.86 | 30.49 | 21.14 | 17 | 14.01 | 15.92 | 12.7 | 12.51 | 11.19 | 7.59 | 17.041 | -55.46% |  |  |  | 181631000 |  |  |  | 56876535.789
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0.003 |  |  |  |  | 189152000
(d) Other Systems | 0.9 | 0.83 | 0 | 0 | 0 | 0 | 0.19 | 0 | 0 | 0 | 0.192 |  |  |  |  | 161736000 |  |  |  | 650837.655
Total of (a+b+c+d) | 1003.88 | 87.34 | 86.87 | 97.4 | 104.93 | 94.59 | 78.97 | 82.24 | 70.32 | 71.89 | 177.843 | -59.58% | 1003.88 | 70.32 |  | 172536000 | 70.7944 | 1 | 0 | 593573954.247
[10 empty] | 64.3 | [5 empty] | 154320000
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 58.45% | 77.09% | 69.04% | 66.04% | 63.55% | 66.55% | 73.33% | 65.51% | 65.37% | 64.85% | 66.98% | -3.177%
24 hours | 76.11% | 99.9% | 99.72% | 99.98% | 99.89% | 99.89% | 99.99% | 99.95% | 99.94% | 99.96% | 97.53% | 2.488%
HV Faults:U/G no damage 3 hours | 96.66% | 98.55% | 94.69% | 89.31% | 97.79% | 98.49% | 94.38% | 98.36% | 98.76% | 95.67% | 96.27% | -0.6191%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV Faults: U/G damage 3 hours | 93.77% | 94.97% | 92.67% | 91.85% | 94.09% | 93.75% | 94.6% | 95.04% | 94.54% | 92.58% | 93.79% | -1.286%
24 hours | 99.93% | 99.97% | 99.98% | 99.98% | 99.99% | 99.99% | 99.99% | 100% | 100% | 100% | 99.98% | 0.017%
HV Faults: O/H no damage 3 hours | 69.22% | 88.26% | 92.19% | 94.01% | 90.15% | 91.99% | 95.06% | 93.55% | 97.31% | 92.85% | 90.46% | 2.643%
24 hours | 91.56% | 99.96% | 99.98% | 100% | 99.98% | 100% | 100% | 100% | 100% | 100% | 99.15% | 0.8593%
HV Faults: O/H damage 3 hours | 53.67% | 85.36% | 78.71% | 85.25% | 83.55% | 83.52% | 87.6% | 85.68% | 87.37% | 82.25% | 81.3% | 1.173%
24 hours | 69.91% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 96.99% | 3.102%
HV Faults: Other 3 hours | 84.68% | 89.93% | 85.45% | 86.79% | 80.88% | 95.15% | 96.56% | 94.92% | 94.53% |  | 89.88%
24 hours | 99.46% | 99.95% | 100% | 99.96% | 99.86% | 100% | 100% | 100% | 100% |  | 99.91%
HV Faults: Total 3 hours | 75.74% | 91.86% | 89.2% | 90.83% | 90.04% | 91.46% | 93.74% | 93.31% | 94.08% | 91.33% | 90.16% | 1.299%
24 hours | 87.7% | 99.98% | 99.99% | 99.99% | 99.98% | 100% | 100% | 100% | 100% | 100% | 98.76% | 1.251%
EHV Faults: 3 hours | 58.97% | 99.99% | 94.54% | 98.28% | 98.7% | 98.73% | 100% | 99.92% | 100% | 100% | 94.91% | 5.36%
24 hours | 82.7% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.27% | 1.76%
132kV F'lts: 3 hours | 55.29% | 100% | 100% | 93.61% | 100% | 100% | 100% | 100% | 99.99% | 100% | 94.89% | 5.386%
24 hours | 80.48% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.05% | 1.991%
Total Faults:3 hours | 65.23% | 91.64% | 87.28% | 88.84% | 87.97% | 90.41% | 92.86% | 92.01% | 91.61% | 89.94% | 87.78% | 2.462% | 92.86% | 65.23% |  | 1679359.68
24 hours | 83.83% | 99.97% | 99.96% | 99.99% | 99.97% | 99.98% | 100% | 99.99% | 99.99% | 99.99% | 98.37% | 1.65% | 100% | 83.83% |  | 1867013.28
TOTAL not rest in 3 hrs | 7.74% | 10.65% | 35.2% | 8.36% | 12.72% | 11.16% | 7.14% | 7.99% | 8.39% | 10.06% | 12.22% | -17.68% | 35.2% | 7.14% |  |  |  | 1 | 0
TOTAL not rest in 24 hrs | 0.05% | 0.09% | 16.86% | 0.03% | 0.04% | 0.01% | 0% | 0.01% | 0.01% | 0.01% | 1.633% | -99.39% | 16.86% | 0% |  |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(b) due to plc action
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3(iii) Verified Voltage Complaints per 10,000 Connected Customers | [6 empty] | 0
| 1.701 | 2.072 | 2.215 | 1.557 | 1.101 | 1.087 | 0.865 | 0.987 | 1.107 | 0.736 | 1.3428 | 10 | 2.215 | 0.736 |  |  |  | 1 | 1
* Overall reliability for 1991/2 affected by change in measured length of system
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
EME total distribution system | 26.88 | 15.69 | 15.09 | 15.66 | 17.3 | 16.23 | 16.31 | 16.42 | 15.93 | 17.02 | 17.253 | -30.65% | 26.88 | 15.09 |  |  |  | 1 | 0
5 RELEVANT DATA:
Number of Customers | 2100000 | 2100000 | 2200000 | 2200000 | 2200000 | 2300000 | 2300000 | 2300000 | 2300000 | 2400000
Embedded Gen.Stations | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 2
Emb.Gen.Capacity MWSO | 449 | 449 | 449 | 799 | 570 | 570 | 570 | 570 | 570 | 570
[9 empty] | %age overhead all voltages | 35.31%
Mains in commission (circuit kilometres) as at 30 September 1995
Overhead Line
132kV |  |  | 2243 | 2190 | 2183 | 2183 | 2183 | 2183 | 2183 | 2183
66kV |  |  |  |  | 1272 | 0 | 0
33kV |  |  | 3691 | 3709 | 3615 | 3405 | 3251 | 3054 | 3030 | 3021
25kV |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
22kV |  |  |  |  | 5752 | 0 | 0
11kV |  |  | 13841 | 13792 | 13945 | 13636 | 13228 | 13225 | 13241 | 13249
6.6kV |  |  | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 36
3.3kV | [5 empty] | 0 | 0 | 0
3kV | [5 empty] | 0 | 0 | 0
2.2kV | [5 empty] | 0 | 0 | 0
LV |  |  | 6410 | 6341 | 6143 | 6109 | 5904 | 5725 | 5613 | 5549
TOTAL |  |  |  | 26237 | 32962 | 25943 | 24618 | 24239 | 24118 | 24049
Underground cable
132kV |  |  | 164 | 164 | 193 | 163 | 163 | 163 | 164 | 164
66kV |  |  |  |  | 1138 | 0 | 0
33kV |  |  | 1530 | 1373 | 1360 | 1452 | 1454 | 1473 | 1473 | 1485
25kV |  |  | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6
22kV |  |  |  |  | 10069.91 | 0 | 0
11kV |  |  | 10912 | 11027 | 11189 | 11896 | 12127 | 12300 | 12425 | 12526
6.6kV |  |  | 942 | 890 | 880 | 902 | 898 | 899 | 897 | 897
3.3kV | [5 empty] | 0 | 0
3kV | [5 empty] | 0 | 0
LV |  |  | 26980 | 27044 | 27809 | 27995 | 28412 | 28477 | 28668 | 28975
TOTAL |  |  |  |  | 52644.91 | 42414 | 40417 | 43318 | 43633 | 44053
[9 empty] | 67751 | 68102
Transformers
Primary Voltage
132kV | [6 empty] | 185 | 181 | 180 | 180
33kV | [6 empty] | 685 | 688 | 694 | 701
Distribution pole-mounted | [6 empty] | 22026 | 22535 | 22443 | 22432
Distribution Other | [6 empty] | 15536 | 15987 | 16359 | 18656
Capacity | [9 empty] | 41969
132kV | [6 empty] | 11090 | 11141 | 11185 | 11185
33kV | [6 empty] | 10985 | 11112 | 10998 | 11190
Distribution | [6 empty] | 9349 | 9669 | 9886 | 11283
[7 empty] | 31424 | 31922 | 32069 | 33658
HV O/H length (km) | 13384.2222 | 13455.3333 | 13526.4444 | 13597.5556 | 13668.6667 | 13739.7778 | 13810.8889 | 13882 | 13281 | 13285
HV U/G length (km) | 10674.8889 | 10843.3333 | 11011.7778 | 11180.2222 | 11348.6667 | 11517.1111 | 11685.5556 | 11854 | 13322 | 13423
SECURITY : customer supply interruptions per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 0.68853 | 1.2588 | 1.9179 | 2.9713 | 2.4426 | 2.3964 | 6.5739 | 7.3924 | 8.3043 | 9.7802 | 4.3727 |  | 9.7802 | 0.68853
HV faults: U/G damage | 44.2037 | 46.6351 | 46.5502 | 49.9811 | 53.8918 | 52.2223 | 44.4626 | 54.5605 | 46.3729 | 40.6228 | 47.9503 |  | 54.5605 | 40.6228
HV faults: O/H no damage | 8.8178 | 8.5371 | 12.5074 | 12.717 | 17.5438 | 15.9027 | 18.4688 | 17.728 | 11.5511 | 15.446 | 13.922 |  | 18.4688 | 8.5371
HV faults: O/H damage | 41.5788 | 17.402 | 17.777 | 22.3114 | 23.5634 | 23.6532 | 20.1008 | 18.8381 | 15.7247 | 16.1144 | 21.7064 |  | 41.5788 | 15.7247
HV underground networks | 44.8923 | 47.8939 | 48.4681 | 52.9524 | 56.3344 | 54.6187 | 51.0365 | 61.9529 | 54.6772 | 50.403 | 52.323 |  | 61.9529 | 44.8923 |  |  |  | 1 | 0
HV overhead networks | 50.3967 | 25.9392 | 30.2844 | 35.0284 | 41.1072 | 39.556 | 38.5696 | 36.5661 | 27.2758 | 31.5604 | 35.6283 |  | 50.3967 | 25.9392 |  |  |  | 1 | 0
Availability : customer minutes lost per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 47.2136 | 91.0237 | 125.8652 | 236.1313 | 158.9614 | 123.8158 | 486.1557 | 455.9642 | 498.9491 | 666.915 | 289.0995 |  | 666.915 | 47.2136
HV faults: U/G damage | 3542.9877 | 3832.6775 | 4145.5613 | 4700.9799 | 5013.0999 | 4629.1122 | 3780.9927 | 4344.272 | 3654.9317 | 3527.6764 | 4117.2291 |  | 5013.0999 | 3527.6764
HV faults: O/H no damage | 4305.3678 | 783.4811 | 875.0267 | 841.3277 | 1405.1114 | 1258.8268 | 1172.4082 | 1216.1072 | 654.6194 | 1080.3161 | 1359.2593 |  | 4305.3678 | 654.6194
HV faults: O/H damage | 42181.308 | 1815.1167 | 2140.3999 | 2417.1992 | 2679.8517 | 2725.226 | 2016.742 | 2003.0975 | 1563.813 | 1972.7512 | 6151.5505 |  | 42181.308 | 1563.813
HV underground networks | 3590.2013 | 3923.7012 | 4271.4266 | 4937.1112 | 5172.0613 | 4752.928 | 4267.1484 | 4800.2362 | 4153.8808 | 4194.5914 | 4406.3286 |  | 5172.0613 | 3590.2013 |  |  |  | 1 | 0
HV overhead networks | 46486.6759 | 2598.5978 | 3015.4266 | 3258.5269 | 4084.9632 | 3984.0528 | 3189.1503 | 3219.2047 | 2218.4323 | 3053.0674 | 7510.8098 |  | 46486.6759 | 2218.4323 |  |  |  | 1 | 0
11590.9604
10424.9098
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
| 3557400 | 1719270 | 1639880 | 2018500 | 2113980 | 2234680 | 2186610 | 2141300 | 1758810 | 1867200
| 2108148000 | 183414000 | 191114000 | 214280000 | 230846000 | 217557000 | 181631000 | 189152000 | 161736000 | 172536000

## C
London
Year: | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | ¢ | 2.44 | 2.11 | 2.21 | 2.31 | 1.71 | 1.59 | 2.33 | 1.95 | 1.79 | 1.844
LV faults | 9.03 | 5.88 | 5.28 | 4.96 | 4.89 | 4.05 | 4.77 | 4.67 | 5.33 | 4.39 | 5.325 | [8 empty] | 177728.7442
HV faults: U/G no damage | 0.02 | 0.05 | 1.6 | 0 | 0.23 | 0.85 | 0 | 0.27 | 0.04 | 0 | 0.306
HV faults: U/G damage | 14.49 | 17.04 | 18.03 | 25.29 | 26.26 | 20.41 | 24.83 | 23.35 | 19.43 | 21.3 | 21.043
HV faults: O/H no damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HV faults: O/H damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 791226
HV faults: All other | 1.41 | 4.77 | 3.44 | 2.09 | 2.19 | 1.42 | 2.13 | 2.64 | 5.74 | 4.9 | 3.073 |  |  |  |  | 913331.9
HV faults: Total | 15.93 | 21.85 | 23.06 | 27.37 | 28.68 | 22.68 | 26.96 | 26.27 | 25.21 | 26.2 | 24.421 | 7.285% |  |  |  | 738765.6 |  |  |  | 503072.6
EHV faults | 4.41 | 4.61 | 4.36 | 0 | 1.03 | 0.67 | 1.57 | 1.8 | 1.4 | 0.3 | 2.015 | -85.11% |  |  |  | 689838.4 |  |  |  | 41509
132kV faults | 3.31 | 9.56 | 2.66 | 0 | 1.03 | 0.35 | 1.7 | 2.8 | 1.42 | 1.87 | 2.47 | -24.29% |  |  |  | 767594.3 |  |  |  | 50882
Total of (a) | 32.68 | 44.35 | 37.47 | 34.55 | 37.95 | 29.46 | 36.6 | 37.87 | 35.33 | 34.55 | 36.081 | -4.243% |  |  |  | 645992.4
(b) Planned Outages | 1.88 | 2.33 | 0.65 | 1.24 | 1.76 | 3.59 | 1.92 | 1.31 | 1.56 | 1.64 | 1.788 | -8.277% |  |  |  | 758458.8 |  |  |  | 36832.8
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 776547.6
(d) Other Systems | 6.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.612 |  |  |  |  | 741857.9 |  |  |  | 12607.2
Total of (a+b+c+d) | 40.68 | 46.67 | 38.12 | 35.78 | 39.71 | 33.06 | 38.52 | 39.18 | 36.89 | 36.19 | 38.48 | -5.951% | 46.67 | 33.06 |  | 745514 | 81.3806 | 1 | 0 | 792688
[10 empty] | 34.55 | [5 empty] | 711730
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | ¢ | ¢ | ¢ | 5.54 | 5.36 | [5 empty] | 2.18
LV faults | 19.33 | 18.38 | 17.1 | 16.69 | 18.71 | 16.44 | 16.96 | 16.27 | 18.92 | 16.43 | 17.523 | [8 empty] | 58485272.967
HV faults: U/G no damage | 0.03 | 0.11 | 2.32 | 0 | 0.36 | 1.08 | 0 | 0.4 | 0.01 | 0 | 0.431
HV faults: U/G damage | 19.36 | 23.29 | 25.85 | 30.06 | 31.96 | 25.65 | 30.7 | 25.94 | 18.73 | 13.83 | 24.537
HV faults: O/H no damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HV faults: O/H damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99797950
HV faults: All other | 2.23 | 5.66 | 4.03 | 2.27 | 2.14 | 1.77 | 2.17 | 2.68 | 3.67 | 3.53 | 3.015 |  |  |  |  | 131725670
HV faults: Total | 21.62 | 29.06 | 32.2 | 32.34 | 34.46 | 28.5 | 32.87 | 29.02 | 22.42 | 17.36 | 27.985 | -37.97% |  |  |  | 102287640 |  |  |  | 93403547.565
EHV faults | 3.22 | 8.26 | 1.54 | 0 | 0.8 | 0.31 | 1.71 | 1.16 | 0.9 | 0.45 | 1.835 | -75.48% |  |  |  | 99870400 |  |  |  | 6124549.215
132kV faults | 0.67 | 5.43 | 0.05 | 0 | 0.07 | 0.03 | 0.17 | 1.05 | 0.04 | 1.28 | 0.879 | 45.62% |  |  |  | 112229980 |  |  |  | 2933775.891
Total of (a) | 44.84 | 61.12 | 50.89 | 49.03 | 54.03 | 45.27 | 51.71 | 47.5 | 42.27 | 35.52 | 48.218 | -26.33% |  |  |  | 105398760
(b) Planned Outages | 5.23 | 6.19 | 1.89 | 2.77 | 4.04 | 8.67 | 4.21 | 2.55 | 2.94 | 3.23 | 4.172 | -22.58% |  |  |  | 110106480 |  |  |  | 13924588.188
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99199100
(d) Other Systems | 1.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.124 |  |  |  |  | 90917310 |  |  |  | 413865.996
Total of (a+b+c+d) | 51.31 | 67.31 | 52.78 | 51.8 | 58.06 | 53.94 | 55.92 | 50.05 | 45.21 | 38.76 | 52.514 | -26.19% | 67.31 | 38.76 |  | 79845600 | 70.7944 | 1 | 1 | 175272249.306
[10 empty] | 35.53 | [5 empty] | 73191800
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 58.9% | 80.2% | 54.07% | 53.07% | 44.8% | 40.31% | 39.53% | 46.57% | 39.83% | 43.01% | 50.03% | -14.03%
24 hours | 99.24% | 99.56% | 99.59% | 99.88% | 99.96% | 99.61% | 99.84% | 99.93% | 99.85% | 99.83% | 99.73% | 0.1013%
HV Faults:U/G no damage 3 hours | 76.09% | 30% | 73.56% | # | 97.53% | 93.5% | # | 69.66% | 100% | # | 54.03% | #VALUE!
24 hours | 100% | 100% | 100% | # | 100% | 100% | # | 100% | 100% | 100% | 80% | 25%
HV Faults: U/G damage 3 hours | 82.17% | 78.68% | 81.54% | 92.63% | 88.29% | 88.77% | 88.15% | 89.09% | 92.74% | 95.27% | 87.73% | 8.591%
24 hours | 99.96% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.004%
HV Faults: O/H no damage 3 hours | # | # | # | # | # | # | # | # | # | # | 0% | #VALUE!
24 hours | # | # | # | # | # |  | # | # | # | # | 0% | #VALUE!
HV Faults: O/H damage 3 hours | 100% | # | # | # | # | # | # | # | # | # | 10% | #VALUE!
24 hours | 100% | # | # | # | # | # | # | # | # | # | 10% | #VALUE!
HV Faults: Other 3 hours | [10 empty] | #DIV/0!
24 hours | [10 empty] | #DIV/0!
HV Faults: Total 3 hours | 79.26% | 78.07% | 81.54% | 92.35% | 88.9% | 89.32% | 87.98% | 89.29% | 92.2% | 94.21% | 87.31% | 7.9%
24 hours | 99.96% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.004%
EHV Faults: 3 hours | 94.99% | 67.38% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 96.24% | 3.91%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
132kV F'lts: 3 hours | 100% | 100% | 100% | # | 100% | 100% | 100% | 100% | 100% | 83.41% | 88.34% | -5.582%
24 hours | 100% | 100% | 100% | # | 100% | 100% | 100% | 100% | 100% | 100% | 90% | 11.11%
Total Faults:3 hours | 77.86% | 77.67% | 79.59% | 84.2% | 81.14% | 80.1% | 80.63% | 82.69% | 82.02% | 84.5% | 81.04% | 4.269% | 84.5% | 77.67% |  | 629959.33
24 hours | 99.77% | 99.92% | 99.92% | 99.97% | 99.99% | 99.92% | 99.97% | 99.99% | 99.98% | 99.97% | 99.94% | 0.03002% | 99.99% | 99.77% |  | 745290.3458
TOTAL not rest in 3 hrs | 30.13% | 22.04% | 22.14% | 22.33% | 20.41% | 19.9% | 19.37% | 17.31% | 17.98% | 15.5% | 18.96% | -18.25% | 30.13% | 15.5% |  |  |  | 1 | 1
TOTAL not rest in 24 hrs | 0.34% | 0.33% | 0.23% | 0.08% | 0% | 0.08% | 0.03% | 0.01% | 0.02% | 0.03% | 0.06% | -50% | 0.34% | 0% |  |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC | 0 | 0 | 2 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | N/A
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(b) due to plc action | 0 |  | 0 | 0 | 0 | [6 empty] | N/A
- Voltage Reductions | 0.026 | 0.026 | 0.003 | 0 | 0.003 | 0.001 | 0 | 0 | 0 | 0
- Load Disconnection | 0.003 | 0.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | 0.028 | 0.033 | 0.003 | 0 | 0.003 | 0.001 | 0 | 0 | 0 | 0 |  | N/A
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 0.231 | 0.302 | 0.614 | 0.581 | 0.269 | 0.169 | 0.168 | 0.121 | 0.204 | 0.369 | 0.3028 | 10 | 0.614 | 0.121 |  |  |  | 0 | 0
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
| 14.5 | 14.44 | 14.73 | 16.17 | 17.11 | 15.73 | 14.58 | 14.31 | 14.61 | 14.98 | 15.116 | -25.34% | 17.11 | 14.31 |  |  |  | 1 | 0
5 RELEVANT DATA:
Number of Customers | 1945000 | 1957000 | 1938000 | 1928000 | 1933000 | 1954000 | 1969000 | 1982000 | 2011000 | 2060000 |  | N/A
Embedded Gen.Stations | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | N/A
Emb.Gen.Capacity MWSO | 140 | 140 | 140 | 140 | 132 | 132 | 132 | 132 | 132 | 132 |  | N/A
[9 empty] | %age overhead all voltages | 0.1353%
Mains in commission (circuit kilometres)
Overhead Line
132kV |  |  | 38 | 38 | 38 | 38 | 38 | 26 | 26 | 28
66kV |  |  | 13 | 13 | 13 | 13 | 13 | 12 | 12 | 12
33kV |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25kV
22kV |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11kV |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
6.6kV |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3kV |  |  | 11 | 11 | 11
3kV
2.2kV
LV |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL |  |  | 63 | 52 | 52 | 52 | 52 | 39 | 39 | 41
Underground cable
132kV |  |  | 465 | 467 | 480 | 480 | 485 | 413 | 493 | 492
66kV |  |  | 535 | 540 | 540 | 546 | 570 | 406 | 430 | 424
33kV |  |  | 597 | 622 | 623 | 623 | 623 | 621 | 649 | 650
25kV
22kV |  |  | 276 | 270 | 270 | 278 | 278 | 268 | 256 | 256
11kV |  |  | 6564 | 6603 | 6610 | 6621 | 6651 | 8013 | 8045 | 8126
6.6kV |  |  | 1706 | 1706 | 1706 | 1706 | 1708 | 642 | 639 | 640
3.3kV |  |  | 388 | 383 | 376
3kV
LV |  |  | 19486 | 19514 | 19543 | 19559 | 19590 | 19593 | 19608 | 19673
TOTAL |  |  |  | 30105 | 29629 | 29722 | 29772 | 29813 | 30120 | 30261
30302
Transformers
Primary Voltage
132kV | [6 empty] | 137 | 143 | 146 | 146
33kV | [6 empty] | 267 | 261 | 255 | 255
Distribution pole-mounted | [6 empty] | 0 | 0 | 0 | 0
Distribution Other | [7 empty] | 12869 | 13033 | 13191
Capacity | [9 empty] | 13592
132kV | [6 empty] | 6578 | 6861 | 7041 | 7041
33kV | [6 empty] | 4334 | 4244 | 4154 | 4154
Distribution | [6 empty] | 8939 | 8961 | 9174 | 8274
[7 empty] | 19851 | 20066 | 20369 | 19469
HV O/H length (km) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HV U/G length (km) | 7974.6311 | 8016.8267 | 8059.0222 | 8101.2178 | 8143.4133 | 8185.6089 | 8227.8044 | 8270 | 8684 | 8766
SECURITY : customer supply interruptions per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 0.04878 | 0.12206 | 3.8476 | 0 | 0.54595 | 2.029 | 0 | 0.64709 | 0.09263 | 0 | 0.73332 |  | 3.8476 | 0
HV faults: U/G damage | 35.3409 | 41.5966 | 43.3578 | 60.1874 | 62.3333 | 48.721 | 59.4208 | 55.9609 | 44.9951 | 50.0548 | 50.1969 |  | 62.3333 | 35.3409
HV faults: O/H no damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HV faults: O/H damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HV underground networks | 35.3897 | 41.7187 | 47.2054 | 60.1874 | 62.8792 | 50.7501 | 59.4208 | 56.608 | 45.0877 | 50.0548 | 50.9302 |  | 62.8792 | 35.3897 |  |  |  | 1 | 0
HV overhead networks | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 0 | 0
customer supply interruptions per circuit km
Availability : customer minutes lost per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 7.317 | 26.8523 | 557.9039 | 0 | 85.4531 | 257.8086 | 0 | 95.8646 | 2.3158 | 0 | 103.3515 |  | 557.9039 | 0
HV faults: U/G damage | 4721.8736 | 5685.358 | 6216.3 | 7153.9467 | 7586.3373 | 6122.9532 | 7346.8324 | 6216.8174 | 4337.4056 | 3250.0342 | 5863.7858 |  | 7586.3373 | 3250.0342
HV faults: O/H no damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HV faults: O/H damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HV underground networks | 4729.1905 | 5712.2103 | 6774.2039 | 7153.9467 | 7671.7904 | 6380.7617 | 7346.8324 | 6312.682 | 4339.7213 | 3250.0342 | 5967.1373 |  | 7671.7904 | 3250.0342 |  |  |  | 1 | 1
HV overhead networks | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 0 | 0
thousands of customer minutes lost per circuit km
4539.2396
3835.6575
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
| 791226 | 913331.9 | 738765.6 | 689838.4 | 767594.3 | 645992.4 | 758458.8 | 776547.6 | 741857.9 | 745514
| 99797950 | 131725670 | 102287640 | 99870400 | 112229980 | 105398760 | 110106480 | 99199100 | 90917310 | 79845600

## D
Manweb
Year: | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 0.88 | 1.43 | 1.279 | 1.6 | 1.39 | 1.11 | 1.16 | 1.29 | 1.11 | 1.29 | 1.2539
LV faults | 4.62 | 4.76 | 4.28 | 4.75 | 4.72 | 5.19 | 4.32 | 4.62 | 4.29 | 4.39 | 4.594 | [8 empty] | 153330.6763
HV faults: U/G no damage | 3.55 | 2.9 | 3.39 | 3.56 | 2.27 | 1.13 | 2.71 | 1.06 | 2.33 | 0.73 | 2.363
HV faults: U/G damage | 6.65 | 8.09 | 8.96 | 7.68 | 7.82 | 10.78 | 9.86 | 8.4 | 8.58 | 13.56 | 9.038
HV faults: O/H no damage | 13.82 | 11.17 | 19.75 | 12.2 | 10.77 | 11.52 | 11.06 | 8.36 | 10.35 | 7.47 | 11.647
HV faults: O/H damage | 17.69 | 11.67 | 10.11 | 13.18 | 9.94 | 8.05 | 11.54 | 15.81 | 7.85 | 8.81 | 11.465 |  |  |  |  | 1065388.9
HV faults: All other | 3.3 | 3.76 | 3.85 | 3.28 | 3.14 | 4.13 | 3.41 | 3.89 | 3.08 | 5.44 | 3.728 |  |  |  |  | 967600
HV faults: Total | 45.01 | 37.59 | 46.06 | 39.9 | 33.94 | 35.6 | 38.58 | 37.52 | 32.19 | 36.01 | 38.24 | -5.832% |  |  |  | 1135055.98 |  |  |  | 535742.4
EHV faults | 14.74 | 12.62 | 19.53 | 10.27 | 14.46 | 10.01 | 5.63 | 8.1 | 2.5 | 6.36 | 10.422 | -38.98% |  |  |  | 1181571.2 |  |  |  | 146012.22
132kV faults | 0 | 1.91 | 0 | 0 | 2.45 | 0.96 | 1.51 | 0.46 | 0 | 1.58 | 0.887 | 78.13% |  |  |  | 942738.4 |  |  |  | 12426.87
Total of (a) | 65.25 | 58.31 | 71.149 | 56.52 | 56.97 | 52.87 | 51.19 | 51.99 | 40.08 | 49.63 | 55.3959 | -10.41% |  |  |  | 834555
(b) Planned Outages | 16.64 | 15.44 | 14.71 | 14.68 | 12.94 | 8.62 | 6 | 5.34 | 4.05 | 3.37 | 10.179 | -66.89% |  |  |  | 784074.9 |  |  |  | 142607.79
(c) Embedded Gen. | 0 | 0 | 0 | 0.19 | 0.02 | 0 | 0 | 0 | 0 | 0.08 | 0.029 |  |  |  |  | 792300.6
(d) Other Systems | 0 | 0 | 0 | 17.25 | 0.11 | 0 | 0 | 0 | 0 | 0 | 1.736 |  |  |  |  | 614730.9 |  |  |  | 24727.65
Total of (a+b+c+d) | 81.89 | 73.75 | 85.859 | 88.64 | 70.04 | 61.5 | 57.19 | 57.33 | 44.13 | 53.08 | 67.3409 | -21.18% | 88.64 | 44.13 |  | 743650.8 | 81.3806 | 1 | 0 | 943446.009
[10 empty] | 49.71 | [5 empty] | 696437.1
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | 1.65 | 2.25 | 1.81 | 2.5 | 1.78 | 1.51 | 1.37 | 1.48 | 1.27 | 1.81 | 1.743
LV faults | 10.82 | 7.8 | 7.02 | 7.37 | 6.52 | 7.24 | 5.85 | 9.9 | 5.43 | 5.76 | 7.371 | [8 empty] | 24601663.359
HV faults: U/G no damage | 4.11 | 3.12 | 3.41 | 4.13 | 2.16 | 1.22 | 2.93 | 1.06 | 1.92 | 0.89 | 2.495
HV faults: U/G damage | 9 | 10.79 | 9.7 | 9.58 | 10.85 | 13.64 | 12.17 | 9.95 | 9.6 | 14.66 | 10.994
HV faults: O/H no damage | 21.96 | 10.47 | 26.63 | 14.31 | 11.68 | 17.1 | 9.9 | 6.64 | 9.53 | 6.52 | 13.474
HV faults: O/H damage | 73.65 | 14.91 | 17.02 | 20.79 | 12.99 | 10.99 | 22.26 | 46.71 | 13.33 | 9.98 | 24.263 |  |  |  |  | 240815100
HV faults: All other | 4.64 | 4.41 | 4.48 | 3.41 | 3.4 | 5.26 | 3.68 | 3.69 | 3.29 | 5.02 | 4.128 |  |  |  |  | 142299520
HV faults: Total | 113.36 | 43.7 | 61.24 | 52.22 | 41.09 | 48.21 | 50.94 | 68.05 | 37.68 | 37.07 | 55.356 | -33.03% |  |  |  | 170921380 |  |  |  | 184757790.924
EHV faults | 14.22 | 8.62 | 13.43 | 8.73 | 16.21 | 7.56 | 3.03 | 4.58 | 1.24 | 3.28 | 8.09 | -59.46% |  |  |  | 161013070 |  |  |  | 27001418.61
132kV faults | 0 | 0.1 | 0 | 0 | 0.53 | 0.04 | 0.21 | 0.06 | 0 | 0.46 | 0.14 | 228.6% |  |  |  | 137022800 |  |  |  | 467268.06
Total of (a) | 140.05 | 62.47 | 83.5 | 70.82 | 66.14 | 64.56 | 61.41 | 84.07 | 45.61 | 48.38 | 72.701 | -33.45% |  |  |  | 119918090
(b) Planned Outages | 45.05 | 45.99 | 45.79 | 43.2 | 35.61 | 23.81 | 16.1 | 12.63 | 9.08 | 7.24 | 28.45 | -74.55% |  |  |  | 106266210 |  |  |  | 94955545.05
(c) Embedded Gen. | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.014 |  |  |  |  | 133639400
(d) Other Systems | 0 | 0 | 0 | 6.67 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0.673 |  |  |  |  | 76183170 |  |  |  | 2292951.123
Total of (a+b+c+d) | 185.1 | 108.46 | 129.29 | 120.79 | 101.8 | 88.37 | 77.51 | 96.7 | 54.69 | 55.66 | 101.837 | -45.34% | 185.1 | 54.69 | 63.46 | 77979660 | 70.7944 | 1 | 0 | 339894124.473
[10 empty] | 48.42 | [5 empty] | 67836420
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 68.05% | 72.57% | 74.91% | 76.85% | 80.62% | 80.24% | 81.9% | 79.89% | 82.42% | 77.62% | 77.51% | 0.1458%
24 hours | 97.66% | 99.7% | 99.79% | 99.68% | 99.95% | 99.96% | 99.7% | 97.98% | 99.99% | 100% | 99.44% | 0.5621%
HV Faults:U/G no damage 3 hours | 91.54% | 85.44% | 91.56% | 88.92% | 97.63% | 92.83% | 87.46% | 95.78% | 89.03% | 82.14% | 90.23% | -8.969%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV Faults: U/G damage 3 hours | 77.52% | 82.8% | 91.72% | 85.7% | 82.84% | 85.75% | 86.59% | 87.42% | 89.17% | 88.28% | 85.78% | 2.916%
24 hours | 99.94% | 99.9% | 99.91% | 99.98% | 100% | 99.92% | 100% | 100% | 100% | 100% | 99.97% | 0.03501%
HV Faults: O/H no damage 3 hours | 93.2% | 90.76% | 84.25% | 85.42% | 91.49% | 80.18% | 92.99% | 94.01% | 88.83% | 89.9% | 89.1% | 0.8945%
24 hours | 98.63% | 100% | 99.84% | 99.65% | 99.3% | 99% | 99.67% | 99.97% | 100% | 100% | 99.61% | 0.3956%
HV Faults: O/H damage 3 hours | 58.09% | 78.19% | 70.31% | 77.41% | 83.36% | 81.63% | 76.07% | 67.44% | 74.26% | 80.5% | 74.73% | 7.727%
24 hours | 92.26% | 99.98% | 99.97% | 100% | 100% | 99.72% | 97.25% | 95.51% | 100% | 100% | 98.47% | 1.555%
HV Faults: Other 3 hours | [10 empty] | #DIV/0!
24 hours | [10 empty] | #DIV/0!
HV Faults: Total 3 hours | 75.31% | 84.03% | 83.62% | 83.33% | 86.82% | 82.88% | 85.08% | 80.75% | 85.24% | 86.81% | 83.39% | 4.105%
24 hours | 96.5% | 99.98% | 99.9% | 99.89% | 99.75% | 99.51% | 99.08% | 98.1% | 100% | 100% | 99.27% | 0.7344%
EHV Faults: 3 hours | 89.9% | 97.04% | 98.29% | 97.62% | 88.59% | 97.55% | 98.19% | 99.15% | 94.08% | 100% | 96.04% | 4.122%
24 hours | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.001%
132kV F'lts: 3 hours | n/a | 100% | n/a | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 80% | 25%
24 hours | n/a | 100% | n/a | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 80% | 25%
Total Faults:3 hours | 76.22% | 86.15% | 86.96% | 85.2% | 87.17% | 85.65% | 86.62% | 83.69% | 85.41% | 87.87% | 85.09% | 3.262% | 87.87% | 76.22% |  | 653445.958
24 hours | 97.39% | 99.96% | 99.92% | 99.88% | 99.85% | 99.67% | 99.27% | 98.4% | 100% | 100% | 99.43% | 0.5692% | 100% | 97.39% |  | 743650.8
TOTAL not rest in 3 hrs | 16.54% | 20.21% | 23.78% | 13.85% | 13.04% | 14.8% | 12.83% | 16.31% | 14.59% | 12.13% | 14.91% | -18.62% | 23.78% | 12.13% | 11.14% |  |  | 1 | 1
TOTAL not rest in 24 hrs | 0.09% | 1.15% | 2.61% | 0.04% | 0.08% | 0.12% | 0.15% | 1.6% | 0% | 0% | 0.566% | -100% | 2.61% | 0% | 0% |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0%
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0%
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(b) due to plc action
- Voltage Reductions | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
-Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 2.2 | 1.84 | 1.63 | 2.85 | 2.56 | 2.01 | 1.61 | 2.54 | 1.66 | 2 | 2.09 | 10 | 2.85 | 1.61 |  |  |  | 1 | 0
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
Total distribution system | 20.03 | 18.37 | 21.646 | 18.12 | 17.96 | 17.96 | 16.54 | 17.11 | 15 | 15.24 | 17.7976 | -13.51% | 21.646 | 15 | 15.97 |  |  | 1 | 0
5 RELEVANT DATA:
Number of Customers | 1301000 | 1312000 | 1322000 | 1333000 | 1346000 | 1357000 | 1371000 | 1382000 | 1393000 | 1401000
Embedded Gen.Stations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emb.Gen.Capacity MWSO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Data Unavailable | [8 empty] | %age overhead all voltages | 47.25%
Mains in commission (circuit kilometres)
Overhead Line
132kV |  |  | 1253.95 | 1235 | 1235 | 1275 | 1300 | 1299 | 1299 | 1299
66kV
33kV |  |  | 1922.433 | 1944 | 1959 | 1963 | 1984 | 2021 | 2006 | 2006
25kV
22kV
11kV |  |  | 12851.33 | 12903 | 12964 | 13018 | 13061 | 13069 | 13052 | 13052
6.6kV |  |  | 45.401 | 45 | 45 | 45 | 2 | 2 | 2 | 2
3.3kV
3kV
2.2kV
LV |  |  | 5105.507 | 5092 | 5081 | 5093 | 5093 | 5141 | 5112 | 5088
TOTAL |  |  |  | 21178.621 | 21219 | 21284 | 21394 | 21532 | 21471 | 21477
Underground cable
132kV |  |  | 213.074 | 211 | 211 | 212 | 213 | 213 | 213 | 213
66kV
33kV |  |  | 1387.178 | 1404 | 1413 | 1418 | 1427 | 1455 | 1491 | 1501
25kV
22kV
11kV |  |  | 4706.065 | 4769 | 4895 | 4974 | 4984 | 5044 | 5143 | 5172
6.6kV |  |  | 1136.547 | 1159 | 1172 | 1184 | 1174 | 1174 | 1149 | 1149
3.3kV
3kV
LV |  |  | 15186.726 | 15290 | 15473 | 15640 | 15663 | 15705 | 15846 | 15939
TOTAL |  |  |  |  | 22629.59 | 22833 | 23164 | 23428 | 23842 | 23974
45451
Transformers
Primary Voltage
132kV | [6 empty] | 78 | 78 | 78 | 79
33kV | [6 empty] | 602 | 597 | 611 | 611
Distribution pole-mounted | [6 empty] | 30836 | 31186 | 31280 | 31455
Distribution Other | [6 empty] | 9536 | 9627 | 9663 | 9712
Capacity | [7 empty] | 41488 | 41632 | 41857
132kV | [6 empty] | 6559 | 6685 | 6685 | 6775
33kV | [6 empty] | 4710 | 4893 | 5003 | 5003
Distribution | [6 empty] | 5389 | 5427 | 5420 | 5449
[7 empty] | 16657 | 17005 | 17108 | 17227
HV O/H length (km) | 12841.718 | 12849.577 | 12857.436 | 12865.295 | 12873.154 | 12881.013 | 12888.872 | 12896.731 | 13054 | 13054
HV U/G length (km) | 5762.8027 | 5774.204 | 5785.6053 | 5797.0067 | 5808.408 | 5819.8093 | 5831.2107 | 5842.612 | 6292 | 6321
SECURITY : customer supply interruptions per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 8.0144 | 6.5893 | 7.7461 | 8.1861 | 5.2603 | 2.6348 | 6.3716 | 2.5073 | 5.1584 | 1.618 | 5.4086 |  | 8.1861 | 1.618
HV faults: U/G damage | 15.0129 | 18.3819 | 20.4734 | 17.6599 | 18.1215 | 25.1356 | 23.1823 | 19.8692 | 18.9955 | 30.0547 | 20.6887 |  | 30.0547 | 15.0129
HV faults: O/H no damage | 14.0011 | 11.4051 | 20.3069 | 12.6407 | 11.261 | 12.1362 | 11.7646 | 8.9585 | 11.0445 | 8.0171 | 12.1536 |  | 20.3069 | 8.0171
HV faults: O/H damage | 17.9218 | 11.9156 | 10.3951 | 13.6561 | 10.3931 | 8.4806 | 12.2752 | 16.9418 | 8.3768 | 9.4552 | 11.9811 |  | 17.9218 | 8.3768
HV underground networks | 23.0273 | 24.9712 | 28.2195 | 25.846 | 23.3819 | 27.7704 | 29.5538 | 22.3765 | 24.1539 | 31.6727 | 26.0973 |  | 31.6727 | 22.3765 |  |  |  | 0 | 0
HV overhead networks | 31.9229 | 23.3207 | 30.702 | 26.2967 | 21.6541 | 20.6168 | 24.0398 | 25.9003 | 19.4213 | 17.4723 | 24.1347 |  | 31.9229 | 17.4723 |  |  |  | 1 | 1
Availability : customer minutes lost per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 927.8662 | 708.9185 | 779.1786 | 949.6781 | 500.5434 | 284.4664 | 688.8844 | 250.7303 | 425.0731 | 197.2615 | 571.26 |  | 949.6781 | 197.2615
HV faults: U/G damage | 2031.8239 | 2451.6765 | 2216.4319 | 2202.8852 | 2514.3034 | 3180.4272 | 2861.3389 | 2353.5535 | 2125.3655 | 3249.2738 | 2518.708 |  | 3249.2738 | 2031.8239
HV faults: O/H no damage | 2224.7771 | 1069.0344 | 2738.0933 | 1482.6889 | 1221.2454 | 1801.4655 | 1053.0712 | 711.5353 | 1016.9519 | 699.7487 | 1401.8612 |  | 2738.0933 | 699.7487
HV faults: O/H damage | 7461.5133 | 1522.3785 | 1749.9943 | 2154.0952 | 1358.2173 | 1157.7839 | 2367.8147 | 5005.394 | 1422.4521 | 1071.0878 | 2527.0731 |  | 7461.5133 | 1071.0878
HV underground networks | 2959.6901 | 3160.5949 | 2995.6105 | 3152.5632 | 3014.8468 | 3464.8936 | 3550.2233 | 2604.2838 | 2550.4387 | 3446.5354 | 3089.968 |  | 3550.2233 | 2550.4387 |  |  |  | 0 | 0
HV overhead networks | 9686.2904 | 2591.4129 | 4488.0877 | 3636.7841 | 2579.4627 | 2959.2494 | 3420.8859 | 5716.9294 | 2439.404 | 1770.8365 | 3928.9343 |  | 9686.2904 | 1770.8365 |  |  |  | 1 | 1
6926.7324
6086.5198
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
| 1065388.9 | 967600 | 1135055.98 | 1181571.2 | 942738.4 | 834555 | 784074.9 | 792300.6 | 614730.9 | 743650.8
| 240815100 | 142299520 | 170921380 | 161013070 | 137022800 | 119918090 | 106266210 | 133639400 | 76183170 | 77979660

## E
Midlands
Year: | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 0.13 | 0.16 | 0.16 | 0.19 | 0.21 | 0.31 | 0.3 | 0.26 | 0.25 | 0.29 | 0.226
LV faults | 5.2656 | 5.71 | 5.34 | 7.9 | 10.92 | 13.33 | 12.19 | 10.03 | 10.07 | 8.32 | 8.9076 | [8 empty] | 297301.2889
HV faults: U/G no damage | 0.99 | 0.82 | 0.86 | 0.5 | 2.83 | 1.38 | 3.72 | 4.28 | 5.02 | 2.17 | 2.257
HV faults: U/G damage | 28.32 | 27.8 | 21.27 | 28.69 | 26.34 | 30.27 | 28.48 | 28.21 | 30.5 | 35.52 | 28.54
HV faults: O/H no damage | 7.71 | 8.42 | 14.06 | 14.13 | 8.95 | 13.69 | 19.02 | 14.18 | 9.27 | 13.98 | 12.341
HV faults: O/H damage | 29.9 | 16.85 | 17.79 | 21.89 | 19.29 | 19.02 | 21.89 | 21.64 | 17.34 | 17.37 | 20.298 |  |  |  |  | 3603734.0371
HV faults: All other | 24.0909 | 18.4 | 20.92 | 21.33 | 20.68 | 23.66 | 21.59 | 22.54 | 21.58 | 27.61 | 22.2401 |  |  |  |  | 2359992
HV faults: Total | 91.0109 | 72.29 | 74.9 | 86.56 | 78.08 | 88.04 | 94.7 | 90.85 | 83.7 | 96.64 | 85.6771 | 12.8% |  |  |  | 2795904 |  |  |  | 1936302.2751
EHV faults | 35.1755 | 13.92 | 23.68 | 13.47 | 11.2 | 24.77 | 17.52 | 17.7 | 15.64 | 19.33 | 19.2406 | 0.4649% |  |  |  | 2732412 |  |  |  | 434836.45
132kV faults | 22.2301 | 3.51 | 10.14 | 5.4 | 9.16 | 0.7 | 10.88 | 3.14 | 1.64 | 8.14 | 7.494 | 8.62% |  |  |  | 2669040 |  |  |  | 169364.6298
Total of (a) | 153.6821 | 95.42 | 114.06 | 113.33 | 109.36 | 126.84 | 135.29 | 121.72 | 111.05 | 132.43 | 121.3182 | 9.159% |  |  |  | 3048540
(b) Planned Outages | 16.3053 | 14.86 | 10.98 | 12.01 | 11.96 | 11.73 | 12.26 | 10.26 | 9.77 | 7.26 | 11.7395 | -38.16% |  |  |  | 3246100 |  |  |  | 265313.4479
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2969550
(d) Other Systems | 0 | 0 | 4.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.441 |  |  |  |  | 2730532 |  |  |  | 9966.6
Total of (a+b+c+d) | 169.9875 | 110.28 | 129.44 | 125.34 | 121.32 | 138.57 | 147.55 | 131.98 | 120.82 | 139.69 | 133.4977 | 4.638% | 169.9875 | 110.28 |  | 3156994 | 81.3806 | 0 | 0 | 3017049.0473
[10 empty] | 132.43 | [5 empty] | 2992918
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults |  |  |  |  | 0.91838 | [5 empty] | 0.91838
LV faults | 11.9379 | 9.81 | 9.67 | 13.51 | 15.92 | 17.72 | 16.24 | 17.66 | 16.37 | 12.73 | 14.1568 | [8 empty] | 47250107.6277
HV faults: U/G no damage | 0.61 | 0.33 | 0.43 | 0.18 | 2.12 | 1.07 | 2.95 | 2.84 | 3.26 | 1.98 | 1.577
HV faults: U/G damage | 28.37 | 22.19 | 18.6 | 24.41 | 24.32 | 24.77 | 21.9 | 21.42 | 24.08 | 32.67 | 24.273
HV faults: O/H no damage | 21.81 | 6.79 | 11.21 | 13.62 | 8.22 | 16.26 | 9.01 | 7.84 | 4.68 | 9.06 | 10.85
HV faults: O/H damage | 178.47 | 16.81 | 21.55 | 34.61 | 21.46 | 24.36 | 26 | 21.96 | 15.34 | 17.52 | 37.808 |  |  |  |  | 843251200
HV faults: All other | 33.65 | 11.94 | 17.65 | 15.51 | 16.59 | 21.18 | 13.94 | 12.74 | 10.14 | 21.11 | 17.445 |  |  |  |  | 252819600
HV faults: Total | 262.9 | 58.05 | 69.45 | 88.33 | 72.7 | 87.64 | 73.8 | 66.8 | 57.49 | 82.34 | 91.95 | -10.45% |  |  |  | 263995200 |  |  |  | 306894986.55
EHV faults | 23.7208 | 4.43 | 6.55 | 3.45 | 1.78 | 13.4 | 1.75 | 4.7 | 2.19 | 4.79 | 6.6761 | -28.25% |  |  |  | 314181600 |  |  |  | 22282261.7824
132kV faults | 50.2311 | 0.53 | 2.64 | 3.11 | 2.73 | 0.03 | 2.02 | 1.25 | 0.13 | 0.9 | 6.3571 | -85.84% |  |  |  | 281512000 |  |  |  | 21217672.0967
Total of (a) | 348.78 | 72.8 | 88.31 | 108.4 | 93.12 | 118.79 | 93.81 | 90.4 | 76.18 | 100.76 | 119.135 | -15.42% |  |  |  | 332860000
(b) Planned Outages | 48.9821 | 45.34 | 33.78 | 35.72 | 34.82 | 32.51 | 32.16 | 25.81 | 23.51 | 16.19 | 32.8822 | -50.76% |  |  |  | 277134000 |  |  |  | 109748619.9883
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 261472500
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 225299400 |  |  |  | 0
Total of (a+b+c+d) | 397.76 | 118.14 | 122.22 | 144.12 | 127.96 | 151.3 | 125.97 | 116.21 | 99.69 | 116.95 | 152.032 | -23.08% | 397.76 | 99.69 |  | 264307000 | 70.7944 | 1 | 0 | 507426412.128
[10 empty] | 100.76 | [5 empty] | 227717600
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 71.63% | 71.32% | 70.42% | 72.13% | 77.26% | 80.32% | 80.08% | 73.74% | 72.65% | 60.04% | 72.96% | -17.71%
24 hours | 98.38% | 99.81% | 99.73% | 99.79% | 99.99% | 100% | 99.99% | 99.25% | 100% | 99.94% | 99.69% | 0.2528%
HV Faults:U/G no damage 3 hours | 97.52% | 97.13% | 99.57% | 99.8% | 94.48% | 93.98% | 94.6% | 96.7% | 97.77% | 86.94% | 95.85% | -9.295%
24 hours | 100% | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.001%
HV Faults: U/G damage 3 hours | 90.07% | 94.94% | 92.85% | 93.95% | 91.22% | 94.79% | 96.06% | 95.09% | 94.66% | 92.78% | 93.64% | -0.9195%
24 hours | 99.75% | 99.98% | 100% | 99.9% | 99.98% | 100% | 100% | 100% | 100% | 100% | 99.96% | 0.03902%
HV Faults: O/H no damage 3 hours | 76.58% | 90.79% | 88.51% | 87.23% | 86.51% | 86.02% | 96.14% | 93.44% | 94.88% | 89.68% | 88.98% | 0.789%
24 hours | 94% | 100% | 100% | 99.66% | 100% | 99.8% | 99.98% | 100% | 100% | 100% | 99.34% | 0.6603%
HV Faults: O/H damage 3 hours | 62.61% | 85.78% | 81.35% | 76.79% | 82.47% | 81.45% | 82.65% | 84.64% | 86.76% | 83.45% | 80.79% | 3.286%
24 hours | 84.23% | 100% | 99.99% | 99.31% | 99.99% | 99.98% | 99.55% | 99.97% | 100% | 99.99% | 98.3% | 1.718%
HV Faults: Other 3 hours | [10 empty] | #DIV/0!
24 hours | [10 empty] | #DIV/0!
HV Faults: Total 3 hours | 79.19% | 91.95% | 88.02% | 88.04% | 88.36% | 88.98% | 92.17% | 91.94% | 93.49% | 89.13% | 89.13% | 0.003659%
24 hours | 93.59% | 99.99% | 99.99% | 99.73% | 99.98% | 99.94% | 99.89% | 99.98% | 100% | 99.99% | 99.31% | 0.6864%
EHV Faults: 3 hours | 92.07% | 99.44% | 97.49% | 94.93% | 98.2% | 89.14% | 100% | 98.45% | 100% | 97.99% | 96.77% | 1.26%
24 hours | 99.96% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.004335%
132kV F'lts: 3 hours | 80.72% | 100% | 100% | 100% | 100% | 100% | 100% | 90.21% | 100% | 100% | 97.09% | 2.994%
24 hours | 95.77% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.58% | 0.4252%
Total Faults:3 hours | 82.1% | 92.11% | 90.23% | 88.32% | 89.23% | 88.16% | 92.72% | 91.34% | 92.61% | 89.26% | 89.61% | -0.3878% | 92.72% | 82.1% |  | 2817932.8444
24 hours | 95.53% | 99.98% | 99.93% | 99.78% | 99.99% | 99.96% | 99.92% | 99.92% | 100% | 99.99% | 99.5% | 0.4925% | 100% | 95.53% |  | 3156678.3006
TOTAL not rest in 3 hrs | 17.9% | 7.89% | 9.77% | 11.68% | 10.77% | 11.84% | 7.28% | 8.66% | 7.39% | 10.74% | 10.39% | 3.344% | 17.9% | 7.28% |  |  |  | 0 | 0
TOTAL not rest in 24 hrs | 4.47% | 0.02% | 0.07% | 0.22% | 0.01% | 0.04% | 0.08% | 0.08% | 0% | 0.01% | 0.5% | -98% | 4.47% | 0% |  |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | N/A
(b) due to plc action
- Voltage Reductions | 52.5 | 119 | 89.88 | 43.81 | 6.32 | 93.5 | 10.2 | 3.4 | 5.9 | 0
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 107.6
Total | 52.5 | 119 | 89.88 | 43.81 | 6.32 | 190.5 | 10.2 | 3.4 | 5.9 | 107.6 |  | N/A
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 2.0705 | 2.04 | 1.69 | 2.25 | 0.51 | 0.72 | 0.37 | 0.23 | 0.15 | 0.12 | 1.0151 | 10 | 2.25 | 0.12 |  |  |  | 1 | 1
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
Excluding service faults# | 11.24 | 9.72 | 10.07 | 11.26 | 12 | 13.88 | 13.59 | 13.03 | 12.78 | 13.24 | 12.081 | -6.626% | 13.88 | 9.72 |  |  |  | 0 | 0
MEB plc total distribution system | 15.87 | 15.01 | 15.6 | 17.62 | 19.26 | 24.43 | 24.06 | 22.32 | 21.72 | 24.2
Number of Customers | 2120000 | 2140000 | 2160000 | 2180000 | 2200000 | 2200000 | 2200000 | 2250000 | 2260000 | 2260000
Embedded Gen.Stations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
Emb.Gen.Capacity MWSO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0
NOTES N/A - Information not applicable | * - Information not available |  |  | # - Nine year average |  |  |  |  | %age overhead all voltages | 40.24%
Mains in commission (circuit kilometres)
Overhead Line
132kV |  |  | 1369.7 | 1406 | 1406 | 1406 | 1349 | 1348.9 | 1347.1 | 1347.1
66kV |  |  | 786.7 | 788.2 | 793.8 | 793.8 | 764.8 | 767.7 | 767.5 | 775.1
33kV |  |  | 1231.7 | 1204.8 | 1176.7 | 1176.7 | 1093.2 | 1050.3 | 1047.4 | 1027.8
25kV |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
22kV
11kV |  |  | 16153.3 | 16159 | 16163 | 16163 | 14886.4 | 14691.7 | 14618.2 | 14586.3
7kV |  |  | 0 | 0
6.6kV & 7kV |  |  | 63.6 | 63.6 | 45.3 | 45.3 | 14.2 | 13.1 | 9.9 | 5.6
3.3kV
2.2kV
LV |  |  | 7697.2 | 7684.1 | 7680.1 | 7680.1 | 7680.7 | 7680.7 | 7680.7 | 6335.6
TOTAL |  |  |  | 27305.7 | 27305.7 | 27264.9 | 27264.9 | 25552.4 | 25470.8 | 24077.5
Underground cable
132kV |  |  | 256.6 | 257 | 257 | 257 | 294 | 294.2 | 302.3 | 303
66kV |  |  | 15.6 | 15.6 | 17 | 17 | 16.9 | 17.4 | 17.6 | 17.7
33kV |  |  | 718 | 726.8 | 710.2 | 710.2 | 436.7 | 418.9 | 408.4 | 389.5
25kV |  |  | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0
22kV
11kV |  |  | 10536.9 | 10686.6 | 10882.8 | 10882.8 | 10655.7 | 10476.8 | 10745.2 | 11061.8
7kV |  |  | 78 | 78 | 24
6.6kV & 7kV |  |  | 878.6 | 854.5 | 768.3 | 768.3 | 635.5 | 520.7 | 479.9 | 446.7
3.3kV
LV |  |  | 24076.8 | 24396.1 | 24852.6 | 24852.6 | 25603.7 | 25987.8 | 26377.6 | 23539.3
TOTAL |  |  | 36565.5 | 37019.6 | 37516.9 | 37492.9 | 37642.5 | 37715.8 | 38331 | 35758
59835.5
Transformers
Primary Voltage
132kV | [6 empty] | 223 | 219 | 220 | 227
33kV | [6 empty] | 361 | 334 | 329 | 332
Distribution pole-mounted | [6 empty] | 33207 | 33675 | 33980 | 34412
Distribution Other | [6 empty] | 14062 | 14206 | 14271 | 14369
Capacity | [7 empty] | 48434 | 48800 | 49340
33kV | [6 empty] | 5600 | 9928 | 9928 | 10378
Distribution | [6 empty] | 9304 | 5141 | 5101 | 5191
[7 empty] | 25042 | 9409 | 9466 | 9542
[8 empty] | 24478 | 24495 | 25111
HV O/H length (km) | 16094.8667 | 16112.3 | 16129.7333 | 16147.1667 | 16217 | 16217 | 16208 | 16208 | 14628.1 | 14591.9
HV U/G length (km) | 10697.4444 | 10811.1667 | 10924.8889 | 11038.6111 | 11494 | 11494 | 11651 | 11651 | 11225.1 | 11508.5
SECURITY : customer supply interruptions per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 1.962 | 1.6231 | 1.7003 | 0.98744 | 5.4167 | 2.6414 | 7.0243 | 8.2654 | 10.107 | 4.2614 | 4.3989 |  | 10.107 | 0.98744
HV faults: U/G damage | 56.1241 | 55.0283 | 42.0537 | 56.6595 | 50.4159 | 57.9381 | 53.7774 | 54.4782 | 61.407 | 69.753 | 55.7635 |  | 69.753 | 42.0537
HV faults: O/H no damage | 10.1555 | 11.1833 | 18.8283 | 19.0767 | 12.1416 | 18.5719 | 25.8169 | 19.6847 | 14.3219 | 21.6523 | 17.1433 |  | 25.8169 | 10.1555
HV faults: O/H damage | 39.384 | 22.3798 | 23.8233 | 29.5533 | 26.1688 | 25.8026 | 29.7125 | 30.0407 | 26.7898 | 26.9027 | 28.0558 |  | 39.384 | 22.3798
HV underground networks | 58.086 | 56.6514 | 43.754 | 57.6469 | 55.8326 | 60.5794 | 60.8016 | 62.7435 | 71.514 | 74.0143 | 60.1624 |  | 74.0143 | 43.754 |  |  |  | 0 | 0
HV overhead networks | 49.5395 | 33.5631 | 42.6517 | 48.63 | 38.3104 | 44.3744 | 55.5294 | 49.7254 | 41.1117 | 48.555 | 45.1991 |  | 55.5294 | 33.5631 |  |  |  | 0 | 0
Availability : customer minutes lost per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 120.8887 | 65.3213 | 85.0169 | 35.548 | 405.7769 | 204.8025 | 557.0337 | 548.4508 | 656.3505 | 388.8257 | 306.8015 |  | 656.3505 | 35.548
HV faults: U/G damage | 5622.3148 | 4392.3659 | 3677.4745 | 4820.697 | 4654.9504 | 4741.0823 | 4135.2674 | 4136.5548 | 4848.135 | 6415.6232 | 4744.4465 |  | 6415.6232 | 3677.4745
HV faults: O/H no damage | 2872.7917 | 901.8328 | 1501.1779 | 1838.8118 | 1115.1261 | 2205.8334 | 1222.9763 | 1088.3514 | 723.0467 | 1403.2169 | 1487.3165 |  | 2872.7917 | 723.0467
HV faults: O/H damage | 23507.8928 | 2232.667 | 2885.8506 | 4672.634 | 2911.266 | 3304.6803 | 3529.1214 | 3048.4946 | 2369.9865 | 2713.5054 | 5117.6099 |  | 23507.8928 | 2232.667
HV underground networks | 5743.2035 | 4457.6873 | 3762.4914 | 4856.245 | 5060.7273 | 4945.8848 | 4692.3011 | 4685.0056 | 5504.4855 | 6804.4489 | 5051.248 |  | 6804.4489 | 3762.4914 |  |  |  | 0 | 0
HV overhead networks | 26380.6845 | 3134.4997 | 4387.0285 | 6511.4458 | 4026.3921 | 5510.5137 | 4752.0977 | 4136.846 | 3093.0333 | 4116.7223 | 6604.9264 |  | 26380.6845 | 3093.0333 |  |  |  | 1 | 0
792222.02
7922.2202
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
| 3603734.0371 | 2359992 | 2795904 | 2732412 | 2669040 | 3048540 | 3246100 | 2969550 | 2730532 | 3156994
| 843251200 | 252819600 | 263995200 | 314181600 | 281512000 | 332860000 | 277134000 | 261472500 | 225299400 | 264307000

## F
Northern
Year: | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 1.6071 | 1.8852 | 1.48 | 1.44 | 1.61 | 1.83 | 2.05 | 1.42 | 2.04 | 1.21 | 1.6572
LV faults | 6.3302 | 6.5404 | 5.9 | 6.36 | 6.19 | 5.93 | 6.69 | 6.39 | 6.42 | 8.59 | 6.5341 | [8 empty] | 218082.9608
HV faults: U/G no damage | 0.22 | 0.62 | 0.61 | 0.18 | 0.92 | 0.56 | 0.6 | 0.88 | 1.38 | 1.4 | 0.737
HV faults: U/G damage | 24.35 | 25.53 | 24.11 | 28.45 | 24.66 | 21.12 | 22.7 | 27.15 | 23.68 | 26.5 | 24.825
HV faults: O/H no damage | 13.04 | 5.37 | 5.45 | 5.78 | 7.72 | 8.1 | 6.3 | 8.01 | 7.48 | 8.71 | 7.596
HV faults: O/H damage | 17.28 | 10.07 | 12.63 | 10.71 | 8.97 | 11.66 | 9.89 | 13.05 | 12.76 | 11 | 11.802 |  |  |  |  | 1513768
HV faults: All other | 15.774 | 13.6936 | 15.2 | 10.75 | 13.76 | 12.12 | 13.52 | 13.68 | 15.41 | 11.51 | 13.5418 |  |  |  |  | 1276037
HV faults: Total | 70.664 | 55.2836 | 58 | 55.87 | 57.46 | 53.58 | 53.02 | 62.77 | 60.71 | 59.12 | 58.6478 | 0.8052% |  |  |  | 1235022.1498 |  |  |  | 856623.3101
EHV faults | 7.476 | 6.6666 | 4.88 | 3.47 | 8.21 | 5.19 | 9.19 | 5.02 | 9.98 | 7.83 | 6.7913 | 15.3% |  |  |  | 1142137.5 |  |  |  | 99194.6637
132kV faults | 7.6634 | 3.6961 | 0.77 | 0 | 3.36 | 0 | 8.12 | 4.41 | 0 | 4.15 | 3.217 | 29% |  |  |  | 1258224.4947 |  |  |  | 46987.6167
Total of (a) | 93.7408 | 74.0719 | 71.03 | 67.14 | 76.85 | 66.53 | 79.06 | 80.01 | 79.15 | 80.88 | 76.8463 | 5.249% |  |  |  | 1308751.574
(b) Planned Outages | 12.1756 | 16.1935 | 15.67 | 12.66 | 11.87 | 9.56 | 9.96 | 10.06 | 11.83 | 9.02 | 11.8999 | -24.2% |  |  |  | 1283776.9392 |  |  |  | 173812.9503
(c) Embedded Gen. | 0.00014231 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0020142 |  |  |  |  | 1298627.4586
(d) Other Systems | 1.7933 | 0 | 0 | 0 | 0 | 13.86 | 0 | 0 | 1.61 | 0 | 1.7263 |  |  |  |  | 1343278.1279 |  |  |  | 25244.5843
Total of (a+b+c+d) | 107.7099 | 90.2653 | 86.69 | 79.8 | 88.71 | 89.96 | 89.04 | 90.07 | 92.59 | 89.91 | 90.4745 | -0.624% | 107.7099 | 79.8 |  | 1313247.0384 | 81.3806 | 1 | 0 | 1321492.6382
* inc service | [9 empty] | 80.89 | [5 empty] | 1181498.7536
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | 1.85 | 1.88 | 1.55 | 1.54 | 1.93 | 2.16 | 2.08 | 1.59 | 3.48 | 1.46 | 1.952
LV faults | 14.1859 | 13.154 | 12.74 | 12.83 | 11.72 | 12.54 | 12.04 | 9.06 | 11.41 | 12.74 | 12.242 | [8 empty] | 40859210.192
HV faults: U/G no damage | 0.01 | 0.23 | 0.14 | 0.07 | 0.36 | 0.18 | 0.22 | 0.3 | 0.74 | 0.35 | 0.26
HV faults: U/G damage | 23.15 | 18.62 | 19.21 | 25.71 | 20.64 | 16.82 | 17.98 | 19.65 | 19.41 | 22.88 | 20.407
HV faults: O/H no damage | 27.26 | 4.98 | 5.07 | 4.97 | 6.78 | 6.13 | 3.33 | 6.06 | 7.01 | 5.19 | 7.678
HV faults: O/H damage | 101.65 | 12.18 | 16.7 | 17.94 | 11.4 | 15.67 | 9.93 | 20.31 | 23 | 13.34 | 24.212 |  |  |  |  | 345668337
HV faults: All other | 12.9861 | 7.2329 | 10.25 | 7.64 | 9.88 | 8.01 | 8.56 | 8.65 | 9.99 | 7.48 | 9.0679 |  |  |  |  | 137172826.8
HV faults: Total | 165.0561 | 43.2429 | 51.37 | 56.33 | 49.07 | 46.8 | 40.01 | 54.97 | 60.15 | 49.23 | 61.6229 | -20.11% |  |  |  | 145242251.9 |  |  |  | 205674366.7126
EHV faults | 27.5103 | 1.9314 | 0.34 | 0.97 | 6.52 | 1.82 | 3.03 | 1.07 | 3.4 | 2.7 | 4.9292 | -45.22% |  |  |  | 146373937.5 |  |  |  | 16451749.2525
132kV faults | 9.2291 | 1.7279 | 0.12 | 0 | 0.28 | 0 | 7.95 | 0.38 | 0 | 2.36 | 2.2047 | 7.044% |  |  |  | 134261673.62 |  |  |  | 7358487.7491
Total of (a) | 215.9814 | 60.0562 | 64.54 | 70.13 | 67.59 | 61.16 | 63.03 | 67.07 | 78.44 | 68.49 | 81.6488 | -16.12% |  |  |  | 125492341.9
(b) Planned Outages | 29.8836 | 36.9783 | 37.37 | 32.14 | 27.07 | 18.85 | 18.76 | 19.57 | 19.13 | 16.74 | 25.6492 | -34.73% |  |  |  | 117939076.4 |  |  |  | 85607450.6791
(c) Embedded Gen. | 0.00051231 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0020512 |  |  |  |  | 124917378.72
(d) Other Systems | 0.089664 | 0 | 0 | 0 | 0 | 6.24 | 0 | 0 | 0.19 | 0 | 0.65197 |  |  |  |  | 141828350.56 |  |  |  | 2182868.243
Total of (a+b+c+d) | 245.9552 | 97.0344 | 101.95 | 102.27 | 94.66 | 86.26 | 81.8 | 86.64 | 97.76 | 85.24 | 107.957 | -21.04% | 245.9552 | 81.8 |  | 124503589.76 | 70.7944 | 1 | 0 | 360320279.8234
[10 empty] | 68.5 | [5 empty] | 100052744
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 69.71% | 72.06% | 72.89% | 71.05% | 72.75% | 73.69% | 77.9% | 80.31% | 76.16% | 77.21% | 74.37% | 3.815%
24 hours | 99.46% | 99.89% | 99.85% | 100% | 99.95% | 99.99% | 99.97% | 99.36% | 99.22% | 100% | 99.77% | 0.2318%
HV Faults:U/G no damage 3 hours | 99.65% | 100% | 100% | 100% | 92.62% | 100% | 92.72% | 98.55% | 94.96% | 98.62% | 97.71% | 0.9293%
24 hours | 100% | 100% | 100% | 100% | 99.99% | 100% | 100% | 100% | 99.99% | 100% | 100% | 0.002%
HV Faults: U/G damage 3 hours | 91.39% | 94.72% | 92.95% | 91.66% | 92.77% | 92.89% | 95.35% | 95.68% | 94.65% | 93.09% | 93.52% | -0.4545%
24 hours | 99.97% | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.004%
HV Faults: O/H no damage 3 hours | 78.51% | 85.26% | 91.64% | 86.15% | 89.28% | 92.09% | 95.57% | 92.88% | 90.22% | 96.64% | 89.82% | 7.588%
24 hours | 97.54% | 99.99% | 99.99% | 99.99% | 99.98% | 100% | 100% | 100% | 99.21% | 100% | 99.67% | 0.3311%
HV Faults: O/H damage 3 hours | 55.96% | 80.94% | 78.49% | 66.93% | 81.5% | 73.73% | 83.94% | 79.76% | 75.89% | 81.47% | 75.86% | 7.394%
24 hours | 85.25% | 100% | 99.98% | 100% | 100% | 100% | 100% | 99.51% | 98.3% | 100% | 98.3% | 1.725%
HV Faults: Other 3 hours | [10 empty] | #DIV/0!
24 hours | [10 empty] | #DIV/0!
HV Faults: Total 3 hours | 80.31% | 91.61% | 89.92% | 85.95% | 90.52% | 88.54% | 92.28% | 91.62% | 89.99% | 91.59% | 89.23% | 2.641%
24 hours | 95.86% | 99.99% | 100% | 99.99% | 99.98% | 99.99% | 100% | 99.81% | 99.49% | 100% | 99.51% | 0.491%
EHV Faults: 3 hours | 42.81% | 98.41% | 100% | 100% | 87.85% | 100% | 100% | 100% | 100% | 99.99% | 92.91% | 7.625%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 9.518e-05%
132kV F'lts: 3 hours | 71.92% | 100% | 100% | 0% | 100% | 100% | 63% | 100% | 100% | 100% | 83.49% | 19.77%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
Total Faults:3 hours | 75.74% | 90.41% | 88.95% | 84.94% | 88.85% | 88.91% | 88.58% | 91.5% | 89.77% | 91.09% | 87.87% | 3.659% | 91.5% | 75.74% |  | 1196236.7273
24 hours | 96.83% | 99.98% | 99.98% | 100% | 99.98% | 99.99% | 100% | 99.79% | 99.51% | 100% | 99.61% | 0.3949% | 100% | 96.83% |  | 1313247.0384
TOTAL not rest in 3 hrs | 10.75% | 14.34% | 24.26% | 9.585% | 11.05% | 15.06% | 11.42% | 8.5% | 10.23% | 8.91% | 12.13% | -26.52% | 24.26% | 8.5% |  |  |  | 1 | 0
TOTAL not rest in 24 hrs | 0.05189% | 0.2057% | 3.166% | 0.01729% | 0.02% | 0% | 0% | 0.21% | 0.49% | 0% | 0.3934% | -100% | 3.166% | 0% |  |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | *
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | *
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | *
(b) due to plc action
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | *
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | *
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | *
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
|  | 0.34662 | 0.39 | 0.43 | 0.36 | 0.49 | 0.52 | 0.04 | 0.17 | 0.25 | 0.33296 | 9 | 0.52 | 0.04 |  |  |  | 1 | 0
* Overall reliability for 1991/2 affected by change in measured length of system
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
Total distribution system | 15.9127 | 13.7308 | 12.92 | 13.5 | 13.45 | 12.55 | 12.78 | 11.97 | 13.66 | 14.21 | 13.4684 | -6.485% | 15.9127 | 11.97 |  |  |  | 0 | 0
5 RELEVANT DATA:
Number of Customers | 1405412 | 1413651 | 1424642 | 1431250 | 1418357 | 1454815 | 1441798 | 1441798 | 1450781 | 1460624
Embedded Gen.Stations | * | 0 | 0 | 0 | 0 | 90 | 75 | 112 | 102 | 120
Emb.Gen.Capacity MWSO | * | 0 | 0 | 0 | 0 | 72.154 | 62.94 | 602090 | 548590 | 682700
* Data Unavailable | [8 empty] | %age overhead all voltages | 39.13%
Mains in commission (circuit kilometres)
Overhead Line
132kV |  | 664 | 664 | 711.4 | 682.777 | 682.777 | 683.977 | 683.977 | 683.977 | 711
66kV |  | 1163 | 1163 | 1160 | 975.203 | 975.203 | 975.203 | 975.203 | 975.203 | 980
33kV |  | 341 | 340 | 340.5 | 340.451 | 317.257 | 317.257 | 317.257 | 317.257 | 317
25kV
22kV |  | 6013 | 6019 | 6027.6 | 6033.098 | 6034.842 | 6037.357 | 6045.136 | 6045.14 | 6049
11kV |  | 4997 | 5006 | 5016.5 | 5025.661 | 5036.533 | 5050.035 | 5078.596 | 5078.6 | 5079
6.6kV |  | 38 | 38 | 38 | 37.968 | 37.968 | 37.968 | 37.968 | 37.968 | 38
3.3kV
3kV |  |  |  |  | 0 | 0 | 0 | 0
2.2kV |  |  |  |  | 0 | 0 | 0 | 0
LV |  | 4090 | 4086 | 4099 | 4093.338 | 4091.742 | 4091.241 | 4091.961 | 4091.96 | 4091
TOTAL |  |  | 17306 | 17316 | 17393 | 17188.496 | 17193.038 | 17230.098 | 17230.105 | 17265
Underground cable
132kV |  | 69 | 69 | 69 | 74.626 | 74.626 | 74.626 | 74.626 | 74.626 | 69
66kV |  | 398 | 398 | 400.1 | 400.361 | 400.361 | 400.361 | 400.361 | 400.361 | 401
33kV |  | 310 | 311 | 310.5 | 310.921 | 310.921 | 310.921 | 310.921 | 310.921 | 312
25kV
22kV |  | 1951 | 1958 | 1978.8 | 2005.069 | 2029.216 | 2054.56 | 2067.643 | 2067.64 | 2077
11kV |  | 5403 | 5523 | 5693.9 | 5800.417 | 5931.856 | 6054.037 | 6173.183 | 6173.18 | 6223
6.6kV |  | 438 | 433 | 432.8 | 432.76 | 432.76 | 432.76 | 432.76 | 432.76 | 432
3.3kV
3kV |  |  |  |  | 0 | 0 | 0 | 0
LV |  | 14464 | 14692 | 14940.1 | 15134.966 | 16855.607 | 17039.665 | 17247.5 | 17247.5 | 17347
TOTAL |  |  |  | 23033 | 23384 | 23825.2 | 24159.12 | 26706.994 | 26706.988 | 26861
44126
Transformers in commission
Primary voltage | Aggregate Capacity
| (KVA) | OH | GM
over 650 Volts | 7737300 | 0 | 425
650 Volts & under | 5528890 | 14713 | 8720
total | 13266190 | 14713 | 9145
23858
HV O/H length (km) | 6303.5556 | 6981.3333 | 7659.1111 | 8336.8889 | 9014.6667 | 9692.4444 | 10370.2222 | 11048 | 11161.708 | 11166
HV U/G length (km) | 5784.5556 | 6071.3333 | 6358.1111 | 6644.8889 | 6931.6667 | 7218.4444 | 7505.2222 | 7792 | 8673.58 | 8732
SECURITY : customer supply interruptions per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 0.53451 | 1.4436 | 1.3668 | 0.3877 | 1.8825 | 1.1286 | 1.1526 | 1.6283 | 2.3082 | 2.3418 | 1.4175 |  | 2.3418 | 0.3877
HV faults: U/G damage | 59.1606 | 59.4441 | 54.0225 | 61.2788 | 50.4593 | 42.5655 | 43.6081 | 50.2372 | 39.6082 | 44.3272 | 50.4712 |  | 61.2788 | 39.6082
HV faults: O/H no damage | 29.0734 | 10.8737 | 10.1373 | 9.9229 | 12.1466 | 12.1579 | 8.759 | 10.4533 | 9.7224 | 11.3935 | 12.464 |  | 29.0734 | 8.759
HV faults: O/H damage | 38.5267 | 20.3908 | 23.4926 | 18.3866 | 14.1133 | 17.5014 | 13.7503 | 17.0307 | 16.5852 | 14.3891 | 19.4167 |  | 38.5267 | 13.7503
HV underground networks | 59.6951 | 60.8877 | 55.3893 | 61.6665 | 52.3418 | 43.6942 | 44.7607 | 51.8655 | 41.9165 | 46.669 | 51.8886 |  | 61.6665 | 41.9165 |  |  |  | 1 | 0
HV overhead networks | 67.6001 | 31.2645 | 33.6299 | 28.3095 | 26.2598 | 29.6593 | 22.5094 | 27.4839 | 26.3076 | 25.7826 | 31.8807 |  | 67.6001 | 22.5094 |  |  |  | 1 | 0
Availability : customer minutes lost per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 2.4296 | 53.5533 | 31.3694 | 15.0774 | 73.6632 | 36.2774 | 42.2633 | 55.5107 | 123.7756 | 58.5454 | 49.2465 |  | 123.7756 | 2.4296
HV faults: U/G damage | 5624.5095 | 4335.4862 | 4304.3244 | 5537.7055 | 4223.3549 | 3389.9254 | 3454.0654 | 3635.9511 | 3246.6017 | 3827.1962 | 4157.912 |  | 5624.5095 | 3246.6017
HV faults: O/H no damage | 6077.7653 | 1008.4008 | 943.0513 | 853.2335 | 1066.7572 | 920.0998 | 462.9783 | 790.8486 | 911.1486 | 678.9037 | 1371.3187 |  | 6077.7653 | 462.9783
HV faults: O/H damage | 22663.4204 | 2466.3296 | 3106.3032 | 3079.8809 | 1793.6625 | 2352.0332 | 1380.5928 | 2650.5175 | 2989.5033 | 1745.0049 | 4422.7248 |  | 22663.4204 | 1380.5928
HV underground networks | 5626.9391 | 4389.0394 | 4335.6938 | 5552.7828 | 4297.0181 | 3426.2029 | 3496.3287 | 3691.4618 | 3370.3773 | 3885.7416 | 4207.1585 |  | 5626.9391 | 3370.3773 |  |  |  | 1 | 0
HV overhead networks | 28741.1857 | 3474.7304 | 4049.3545 | 3933.1144 | 2860.4197 | 3272.133 | 1843.5711 | 3441.3662 | 3900.6519 | 2423.9085 | 5794.0435 |  | 28741.1857 | 1843.5711 |  |  |  | 1 | 0
6270.3046
5711.6205
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
| 1513768 | 1276037 | 1235022.1498 | 1142137.5 | 1258224.4947 | 1308751.574 | 1283776.9392 | 1298627.4586 | 1343278.1279 | 1313247.0384
| 345668337 | 137172826.8 | 145242251.9 | 146373937.5 | 134261673.62 | 125492341.9 | 117939076.4 | 124917378.72 | 141828350.56 | 124503589.76

## G
NORWEB
Year: | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 4.7 | 3.6 | 3.95 | 3.87 | 4.8 | 5 | 3.9 | 3.3 | 2.1 | 1.6 | 3.682
LV faults | 8.9 | 8 | 8.27 | 8.07 | 8.8 | 8.2 | 6.8 | 8 | 7.4 | 6.5 | 7.894 | [8 empty] | 263472.4333
HV faults: U/G no damage | 0.72 | 0.93 | 1.93 | 1.61 | 1 | 1 | 0.8 | 1.7 | 1.7 | 3.6 | 1.499
HV faults: U/G damage | 17.36 | 18.5 | 16.37 | 15.7 | 18.7 | 18.2 | 22.4 | 22 | 19.4 | 17.7 | 18.633
HV faults: O/H no damage | 3.15 | 2.69 | 4 | 2.62 | 4.3 | 4.5 | 3.8 | 4.8 | 3.4 | 4.3 | 3.756
HV faults: O/H damage | 6.36 | 5.9 | 5.83 | 5.83 | 7.2 | 5.8 | 5.4 | 8 | 7.7 | 7.5 | 6.552 |  |  |  |  | 1211328
HV faults: All other | 4.89 | 4.4 | 4.44 | 3.75 | 4.3 | 6.9 | 4.8 | 4.7 | 5.9 | 5.9 | 4.998 |  |  |  |  | 1301955
HV faults: Total | 32.5 | 32.4 | 32.6 | 29.48 | 35.4 | 36.4 | 37.2 | 41.2 | 38.1 | 39 | 35.428 | 10.08% |  |  |  | 1205796.3 |  |  |  | 780478.84
EHV faults | 4.5 | 5.1 | 4.21 | 4.36 | 5.3 | 4.4 | 4.7 | 5.8 | 6.7 | 4.7 | 4.977 | -5.566% |  |  |  | 1195190 |  |  |  | 109643.31
132kV faults | 2.6 | 7.7 | 1.27 | 1.98 | 9.4 | 1.8 | 3.9 | 9.3 | 0 | 0 | 3.795 | -100% |  |  |  | 1505520 |  |  |  | 83603.85
Total of (a) | 53.2 | 56.8 | 50.3 | 47.76 | 63.6 | 55.7 | 56.5 | 67.6 | 54.3 | 51.9 | 55.766 | -6.933% |  |  |  | 1316480
(b) Planned Outages | 4.4 | 4.7 | 6.39 | 6.69 | 6.1 | 4.8 | 3 | 3.2 | 3.3 | 2.9 | 4.548 | -36.24% |  |  |  | 1303050 |  |  |  | 100192.44
(c) Embedded Gen. | * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1845276
(d) Other Systems | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 | 13 | 0 | 0 | 1.44 |  |  |  |  | 1232640 |  |  |  | 31723.2
Total of (a+b+c+d) | 57.6 | 61.5 | 56.69 | 55.85 | 69.7 | 60.5 | 59.5 | 83.8 | 57.6 | 54.7 | 61.744 | -11.41% | 83.8 | 54.7 |  | 1205041 | 81.3806 | 1 | 1 | 1360220.32
[10 empty] | 51.8 | [5 empty] | 1141154
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | 4.1 | 3.1 | 3.58 | 2.9 | 3.1 | 3.9 | 3.7 | 3 | 2.1 | 1.5 | 3.098
LV faults | 17.3 | 14.8 | 15.13 | 13.2 | 13.4 | 12.2 | 11.8 | 14.1 | 11.7 | 9.4 | 13.303 | [8 empty] | 44400478.587
HV faults: U/G no damage | 0.49 | 1 | 1.3 | 1.5 | 0.4 | 1 | 0.8 | 1.5 | 1.5 | 2.9 | 1.239
HV faults: U/G damage | 18.16 | 18.77 | 17.14 | 13.63 | 14.9 | 15.6 | 21 | 22.5 | 18.3 | 16.7 | 17.67
HV faults: O/H no damage | 3.01 | 3.2 | 3.71 | 2.33 | 4.1 | 3.9 | 3.5 | 5.5 | 6.6 | 4.2 | 4.005
HV faults: O/H damage | 18.34 | 10.9 | 8.88 | 7.44 | 10.2 | 7.5 | 7.4 | 20.2 | 17.8 | 8.8 | 11.746 |  |  |  |  | 184433100
HV faults: All other | 4.68 | 4.11 | 5.05 | 3.4 | 3.5 | 6.2 | 4.5 | 6.8 | 5.4 | 5.9 | 4.954 |  |  |  |  | 158139900
HV faults: Total | 44.7 | 38 | 36.1 | 28.28 | 33.1 | 34.2 | 37.2 | 56.5 | 49.6 | 38.4 | 39.608 | -3.05% |  |  |  | 162715500 |  |  |  | 132196809.432
EHV faults | 2.8 | 3 | 0.98 | 1.6 | 1.2 | 1.9 | 1.2 | 4.2 | 6.5 | 4.2 | 2.758 | 52.28% |  |  |  | 147018000 |  |  |  | 9205180.782
132kV faults | 4.8 | 0.7 | 0.36 | 0.59 | 0.7 | 1.5 | 2.9 | 4.9 | 0 | 0 | 1.645 | -100% |  |  |  | 151200000 |  |  |  | 5490399.705
Total of (a) | 73.7 | 59.6 | 56.15 | 46.57 | 51.6 | 53.6 | 56.8 | 82.7 | 69.9 | 53.5 | 60.412 | -11.44% |  |  |  | 145792000
(b) Planned Outages | 14 | 15.1 | 20.33 | 21.64 | 18.4 | 13.3 | 9.1 | 9.2 | 9.9 | 9.2 | 14.017 | -34.37% |  |  |  | 144321000 |  |  |  | 46783545.693
(c) Embedded Gen. | * | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002 |  |  |  |  | 212272800
(d) Other Systems | 0 | 0 | 0 | 0.49 | 0 | 0 | 0 | 4.5 | 0 | 0 | 0.499 |  |  |  |  | 170986000 |  |  |  | 1666144.3968
Total of (a+b+c+d) | 87.7 | 74.7 | 76.5 | 68.7 | 70 | 67 | 65.9 | 96.4 | 79.9 | 62.7 | 74.95 | -16.34% | 96.4 | 62.7 |  | 138128100 | 70.7944 | 1 | 1 | 250155293.55
Note: * indicates information either not available or inapplicable | [9 empty] | 53.5 | [5 empty] | 117860500
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 77.3% | 78.2% | 78.5% | 81.82% | 84.2% | 83.36% | 78.86% | 76.78% | 81.02% | 84.12% | 80.42% | 4.606%
24 hours | 99.2% | 100% | 99.7% | 99.93% | 99.99% | 99.99% | 99.86% | 99.87% | 99.83% | 100% | 99.84% | 0.1633%
HV Faults:U/G no damage 3 hours | 95.38% | 94.4% | 97.61% | 98.07% | 99.9% | 94.28% | 94.25% | 94.41% | 94.65% | 94.61% | 95.76% | -1.197%
24 hours | 100% | 99.9% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.99% | 0.01%
HV Faults: U/G damage 3 hours | 90.92% | 91.57% | 91.82% | 95.18% | 96.8% | 94.71% | 93.69% | 92.61% | 94.47% | 94.77% | 93.65% | 1.192%
24 hours | 99.96% | 100% | 99.91% | 99.99% | 99.99% | 100% | 99.97% | 99.95% | 100% | 99.99% | 99.98% | 0.014%
HV Faults: O/H no damage 3 hours | 89.96% | 83.93% | 91.4% | 90.98% | 91.1% | 94.51% | 93.64% | 90.42% | 82.36% | 92.96% | 90.13% | 3.144%
24 hours | 99.89% | 100% | 100% | 100% | 100% | 100% | 100% | 99.5% | 98.52% | 100% | 99.79% | 0.2094%
HV Faults: O/H damage 3 hours | 56.76% | 66.59% | 75.29% | 83.36% | 80.7% | 83.97% | 81.19% | 71.5% | 77.93% | 83.85% | 76.11% | 10.16%
24 hours | 99.97% | 99.9% | 99.92% | 100% | 99.99% | 99.99% | 99.97% | 97.28% | 97.16% | 100% | 99.42% | 0.5854%
HV Faults: Other 3 hours | 87.5% | 87.85% | 82.55% | 90.13% | 93.7% | 93.11% | 89.98% | 82.84% | 91.92% | 89.67% | 88.92%
24 hours | 99.97% | 99.9% | 100% | 100% | 99.99% | 100% | 100% | 99.42% | 99.82% | 100% | 99.91%
HV Faults: Total 3 hours | 83.7% | 86.1% | 87.89% | 92% | 92.5% | 92.66% | 91.39% | 87.24% | 89.66% | 91.68% | 89.48% | 2.456%
24 hours | 100% | 99.9% | 99.94% | 99.99% | 99.99% | 100% | 99.98% | 99.32% | 99.27% | 100% | 99.84% | 0.1613%
EHV Faults: 3 hours | 91.7% | 94.2% | 100% | 95.22% | 100% | 93.4% | 98.88% | 92.69% | 89.11% | 89.92% | 94.51% | -4.859%
24 hours | 100% | 99.8% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.98% | 0.02%
132kV F'lts: 3 hours | 61.1% | 99.9% | 100% | 100% | 100% | 100% | 100% | 100% | 33.33% | 50% | 84.43% | -40.78%
24 hours | 100% | 99.9% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.99% | 0.01%
Total Faults:3 hours | 81.7% | 87% | 87.3% | 90.36% | 92.5% | 90.77% | 90.24% | 87.73% | 88.08% | 90.34% | 88.6% | 1.962% | 92.5% | 81.7% |  | 1088634.0394
24 hours | 99.8% | 99.9% | 99.9% | 99.98% | 99.99% | 100% | 99.96% | 99.57% | 99.45% | 100% | 99.86% | 0.1452% | 100% | 99.45% |  | 1205041
TOTAL not rest in 3 hrs | 12.1% | 15.8% | 18.3% | 13% | 12.7% | 9.23% | 9.76% | 12.27% | 11.92% | 9.66% | 11.4% | -15.25% | 18.3% | 9.23% |  |  |  | 1 | 0
TOTAL not rest in 24 hrs | 0.1% | 0.3% | 0.2% | 0.1% | 0.1% | 0% | 0.04% | 0.43% | 0.55% | 0% | 0.145% | -100% | 0.55% | 0% |  |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N\A
- Load Disconnection | nil | nil | nil | nil | nil | 0 | 0 | 0 | 0 | 0 | N\A
TOTAL | nil | nil | nil | nil | nil | 0 | 0 | 0 | 0 | 0
(b) due to plc action
- Voltage Reductions | 0.006 | 0.00047467 | 0.0002 | 0.0002 | 0.0001 | 0.001 | 0.0006 | 0.0063 | 0.0009 | 0 | N\A
- Load Disconnection | nil | nil | nil | nil | nil | 0 | 0 | 0 | 0 | 0 | N\A
- Total | 0.006 | 0.00047467 | 0.0002 | 0.0002 | 0.0001 | 0.001 | 0.0006 | 0.0063 | 0.0009 | 0
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 1.6 | 1.9 | 2.01 | 2.09 | 1.9 | 1.82 | 0.89 | 0.89 | 0.76 | 0.64 | 1.45 | 10 | 2.09 | 0.64 |  |  |  | 1 | 1
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
total distribution system (excluding service faults) | 19.7 | 17.4 | 17.2 | 16.05 | 16.2 | 15.1 | 14.2 | 17.5 | 17.6 | 17.1 | 16.805 | -18.89% | 19.7 | 14.2 |  |  |  | 0 | 0
5 RELEVANT DATA:
(i) Total Connected Customers (000's) | 2103000 | 2117000 | 2127000 | 2140000 | 2160000 | 2176000 | 2190000 | 2202000 | 2140000 | 2203000 | 2846786.6 | 7.044%
Embedded Gen.Stations | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | N\A
Emb.Gen.Capacity MWSO | 392 | 621 | 621 | 589 | 589 | 589 | 589 | 589 | 575 | 575 | N\A
Note: * indicates information either not available or inapplicable | [8 empty] | %age overhead all voltages | 23.7%
Mains in commission (circuit kilometres)
Overhead Line
132kV |  |  | 1572 | 1572 | 1572 | 1572 | 1572 | 1331 | 1331 | 1331
66kV
33kV |  |  | 1357 | 1356 | 1356 | 1346 | 1346 | 1411 | 1412 | 1412
25kV |  |  | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
22kV
11kV |  |  | 7446 | 7474 | 7494 | 7550 | 7550 | 7115 | 7136 | 7114
6.6kV |  |  | 882 | 886 | 883 | 889 | 889 | 894 | 896 | 885
3.3kV |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3kV
2.2kV |  |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LV |  |  | 3389 | 3381 | 3343 | 3278 | 3278 | 3186 | 3180 | 3180
TOTAL |  |  |  | 14653 | 14649 | 14649 | 14636 | 13937 | 13955 | 13923
Underground cable
132kV |  |  | 236 | 233 | 233 | 234 | 234 | 234 | 233 | 233
66kV
33kV |  |  | 1716 | 1719 | 1719 | 1780 | 1780 | 1780 | 1781 | 1790
25kV |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9
22kV
11kV |  |  | 5981 | 6031 | 6090 | 6198 | 6198 | 6218 | 6218 | 6218
6.6kV |  |  | 6440 | 6485 | 6515 | 6568 | 6568 | 6588 | 6588 | 6588
3.3kV |  |  | 28 | 28 | 24 | 24 | 24 | 24 | 1.4 | 1.4
2.2kV |  |  | 31 | 31 | 31 | 36 | 36 | 36 | 0 | 0
LV |  |  | 29150 | 29369 | 29622 | 29859 | 29859 | 29986 | 29986 | 29986
TOTAL |  |  |  |  | 43592 | 44709 | 44247 | 44709 | 44817.4 | 44825.4
58748.4
Transformers
Primary Voltage
132kV | [6 empty] | 143 | 143 | 141 | 144
33kV | [6 empty] | 707 | 671 | 666 | 681
Distribution pole-mounted | [6 empty] | 16104 | 16352 | 16357 | 16390
Distribution Other | [6 empty] | 14364 | 14630 | 14866 | 14970
Capacity | [6 empty] | 31318 | 31796 | 32030 | 32185
132kV | [6 empty] | 9937 | 9658 | 9528 | 9698
33kV | [6 empty] | 12294 | 12434 | 12485 | 12787
Distribution | [6 empty] | 8302 | 8506 | 8666 | 8674
[7 empty] | 30533 | 30598 | 30679 | 31159
HV O/H length (km) | 8170.6667 | 8194 | 8217.3333 | 8240.6667 | 8264 | 8287.3333 | 8310.6667 | 8334 | 8032 | 7999
HV U/G length (km) | 11909.1111 | 11990.6667 | 12072.2222 | 12153.7778 | 12235.3333 | 12316.8889 | 12398.4444 | 12480 | 12807.4 | 12807.4
SECURITY : customer supply interruptions per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 1.2714 | 1.642 | 3.4005 | 2.8348 | 1.7654 | 1.7667 | 1.4131 | 2.9995 | 2.8405 | 6.1924 | 2.6126 |  | 6.1924 | 1.2714
HV faults: U/G damage | 30.6556 | 32.6625 | 28.8422 | 27.6441 | 33.0126 | 32.1536 | 39.5663 | 38.8173 | 32.4156 | 30.4458 | 32.6216 |  | 39.5663 | 27.6441
HV faults: O/H no damage | 8.1076 | 6.9499 | 10.3537 | 6.8038 | 11.2391 | 11.8156 | 10.0136 | 12.6825 | 9.0588 | 11.8426 | 9.8867 |  | 12.6825 | 6.8038
HV faults: O/H damage | 16.3696 | 15.2432 | 15.0906 | 15.1398 | 18.819 | 15.229 | 14.2299 | 21.1375 | 20.5154 | 20.6557 | 17.243 |  | 21.1375 | 14.2299
HV underground networks | 31.927 | 34.3044 | 32.2427 | 30.4789 | 34.778 | 33.9203 | 40.9793 | 41.8168 | 35.2562 | 36.6381 | 35.2342 |  | 41.8168 | 30.4789 |  |  |  | 0 | 0
HV overhead networks | 24.4772 | 22.1931 | 25.4443 | 21.9436 | 30.0581 | 27.0446 | 24.2435 | 33.82 | 29.5742 | 32.4983 | 27.1297 |  | 33.82 | 21.9436 |  |  |  | 0 | 0
Availability : customer minutes lost per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 86.5279 | 176.554 | 229.0465 | 264.1154 | 70.6152 | 176.668 | 141.308 | 264.6635 | 250.6364 | 498.8288 | 215.8964 |  | 498.8288 | 70.6152
HV faults: U/G damage | 3206.8288 | 3313.9183 | 3019.8897 | 2399.9287 | 2630.4146 | 2756.0206 | 3709.3363 | 3969.9519 | 3057.7635 | 2872.5659 | 3093.6618 |  | 3969.9519 | 2399.9287
HV faults: O/H no damage | 774.7263 | 826.7513 | 960.3079 | 605.0724 | 1071.636 | 1024.0206 | 922.3087 | 1453.2037 | 1758.4661 | 1156.7196 | 1055.3213 |  | 1758.4661 | 605.0724
HV faults: O/H damage | 4720.4251 | 2816.1216 | 2298.5267 | 1932.0767 | 2666.0213 | 1969.2704 | 1950.0241 | 5337.221 | 4742.5299 | 2423.603 | 3085.582 |  | 5337.221 | 1932.0767
HV underground networks | 3293.3566 | 3490.4723 | 3248.9362 | 2664.0441 | 2701.0298 | 2932.6886 | 3850.6443 | 4234.6154 | 3308.3998 | 3371.3947 | 3309.5582 |  | 4234.6154 | 2664.0441 |  |  |  | 0 | 0
HV overhead networks | 5495.1514 | 3642.8728 | 3258.8346 | 2537.1491 | 3737.6573 | 2993.291 | 2872.3327 | 6790.4248 | 6500.996 | 3580.3225 | 4140.9032 |  | 6790.4248 | 2537.1491 |  |  |  | 1 | 0
10045.9764
9075.5351
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
| 1211328 | 1301955 | 1205796.3 | 1195190 | 1505520 | 1316480 | 1303050 | 1845276 | 1232640 | 1205041
| 184433100 | 158139900 | 162715500 | 147018000 | 151200000 | 145792000 | 144321000 | 212272800 | 170986000 | 138128100

## H
SEEBOARD
Year: | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | * | 1.36 | 1.43 | 1.2 | 1.1 | 1 | 1.4 | 1.2 | 1 | 1.2 | 1.089
LV faults | 5.2 | 4.63 | 4.37 | 4 | 4.3 | 4.1 | 5.7 | 4.7 | 4 | 4.2 | 4.52 | [8 empty] | 150860.8308
HV faults: U/G no damage | 2.1 | 1.6 | 2 | 1.6 | 3.2 | 3.7 | 4.8 | 2.3 | 3.1 | 1.9 | 2.63
HV faults: U/G damage | 41.2 | 40.2 | 43.7 | 38.8 | 45.6 | 37.4 | 32.7 | 37.2 | 44.6 | 36.4 | 39.78
HV faults: O/H no damage | 8.2 | 6.9 | 9.4 | 5 | 8.9 | 7.9 | 6.4 | 6.6 | 5.5 | 4.8 | 6.96
HV faults: O/H damage | 9.3 | 8.7 | 10.1 | 8.2 | 10.3 | 8.8 | 9.5 | 9.3 | 10.6 | 9.9 | 9.47 |  |  |  |  | 2148090
HV faults: All other | 19.2 | 16.7 | 15.9 | 15 | 15.2 | 17 | 19.7 | 17.6 | 16.2 | 17.4 | 16.99 |  |  |  |  | 1994395.8
HV faults: Total | 79.9 | 74 | 81.1 | 68.6 | 83.3 | 74.8 | 73.1 | 73 | 79.9 | 70.5 | 75.82 | -7.017% |  |  |  | 3121248 |  |  |  | 1621789.8
EHV faults | 6.1 | 7.4 | 9.5 | 6.4 | 7.9 | 8.4 | 5 | 6.4 | 7.2 | 6 | 7.03 | -14.65% |  |  |  | 1960885.956 |  |  |  | 150371.7
132kV faults | 13.1 | 10.3 | 7.8 | 16.5 | 5.2 | 5.3 | 4.2 | 4.7 | 2.6 | 7.5 | 7.72 | -2.85% |  |  |  | 2056080 |  |  |  | 165130.8
Total of (a) | 104.3 | 96.4 | 102.8 | 95.4 | 100.7 | 92.7 | 88 | 88.8 | 93.7 | 88.3 | 95.11 | -7.16% |  |  |  | 1889720
(b) Planned Outages | 7 | 6.51 | 6.24 | 4.2 | 3.3 | 2.3 | 1.2 | 2.2 | 1.8 | 1.6 | 3.635 | -55.98% |  |  |  | 1847332 |  |  |  | 77752.65
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1918280
(d) Other Systems | 0 | 0 | 43.9 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 4.42 |  |  |  |  | 2030330 |  |  |  | 94543.8
Total of (a+b+c+d) | 111.3 | 102.91 | 159.9 | 99.6 | 104 | 95.2 | 89.2 | 91 | 95.5 | 89.9 | 103.851 | -13.43% | 159.9 | 89.2 |  | 1922961 | 81.3806 | 1 | 0 | 2221372.89
* inc service | [9 empty] | 88.3 | [5 empty] | 1888737
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | * | * | 4.9 | 0.99 | 2.41 |  |  | 1.6 | 1.4 | 1 | 1.5375
LV faults | 8.2 | 6.56 | 6.6 | 7 | 7.9 | 7.01 | 13.27 | 8.4 | 6.9 | 7.7 | 7.954 | [8 empty] | 26547501.066
HV faults: U/G no damage | 1.3 | 0.8 | 1.5 | 1.1 | 2.1 | 2.6 | 3.4 | 2 | 1.9 | 1.4 | 1.81
HV faults: U/G damage | 33 | 28.2 | 36.2 | 30 | 34.6 | 27.2 | 29.9 | 32.4 | 32.4 | 30.1 | 31.4
HV faults: O/H no damage | 9.1 | 6.3 | 11.9 | 4.8 | 10.9 | 7.2 | 6.9 | 8.6 | 5 | 4.9 | 7.56
HV faults: O/H damage | 10.6 | 10.1 | 11.2 | 9.4 | 13 | 8.8 | 13.4 | 12.6 | 10.8 | 10.9 | 11.08 |  |  |  |  | 215388000
HV faults: All other | 14 | 12 | 11.9 | 10.9 | 10.3 | 12.4 | 16.4 | 15.5 | 9.8 | 11.6 | 12.48 |  |  |  |  | 186435600
HV faults: Total | 68 | 57.3 | 72.8 | 56.3 | 70.9 | 58.3 | 70 | 71.1 | 60 | 58.9 | 64.36 | -8.484% |  |  |  | 230921600 |  |  |  | 214809802.44
EHV faults | 6.1 | 7.1 | 5.7 | 3.4 | 4.5 | 5.7 | 2.3 | 2.7 | 3.5 | 2 | 4.3 | -53.49% |  |  |  | 165572800.1 |  |  |  | 14351804.7
132kV faults | 5.3 | 3.7 | 0 | 5.6 | 1 | 0.9 | 0.2 | 4.4 | 1.5 | 1.3 | 2.39 | -45.61% |  |  |  | 184454100 |  |  |  | 7976933.31
Total of (a) | 87.7 | 74.7 | 85.1 | 72.4 | 84.3 | 71.9 | 85.8 | 86.6 | 71.9 | 69.9 | 79.03 | -11.55% |  |  |  | 154631500
(b) Planned Outages | 23.9 | 21.52 | 19.3 | 11.7 | 9 | 6.01 | 3.58 | 5.7 | 3.9 | 3.3 | 10.791 | -69.42% |  |  |  | 184940300 |  |  |  | 36016354.539
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 194568400
(d) Other Systems | 0 | 0 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.39 |  |  |  |  | 161150800 |  |  |  | 4639304.31
Total of (a+b+c+d) | 111.6 | 96.2 | 118.3 | 84.1 | 93.3 | 77.9 | 89.3 | 92.3 | 75.8 | 73.2 | 91.2 | -19.74% | 118.3 | 73.2 |  | 156574800 | 70.7944 | 1 | 1 | 304391764.8
[10 empty] | 69.9 | [5 empty] | 149516100
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 71.6% | 76.1% | 74% | 69% | 68.4% | 70.3% | 57% | 66.7% | 70.3% | 69.7% | 69.31% | 0.5627%
24 hours | 99.7% | 100% | 100% | 99.7% | 99.7% | 99.9% | 100% | 100% | 100% | 99.8% | 99.88% | -0.0801%
HV Faults:U/G no damage 3 hours | 98% | 97.9% | 94.8% | 93.6% | 95.9% | 92.4% | 95.3% | 89.7% | 93.4% | 94.2% | 94.52% | -0.3386%
24 hours | 100% | 100% | 100% | 100% | 99.8% | 100% | 100% | 100% | 100% | 100% | 99.98% | 0.02%
HV Faults: U/G damage 3 hours | 94.6% | 95.6% | 94.8% | 94.3% | 95% | 94.8% | 92.8% | 94% | 95.6% | 93.9% | 94.54% | -0.677%
24 hours | 99.9% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.99% | 0.01%
HV Faults: O/H no damage 3 hours | 81.9% | 87.9% | 78.2% | 88.5% | 83.4% | 90.9% | 84.7% | 85.9% | 92% | 85.8% | 85.92% | -0.1397%
24 hours | 100% | 100% | 100% | 100% | 99.7% | 100% | 100% | 100% | 100% | 100% | 99.97% | 0.03001%
HV Faults: O/H damage 3 hours | 84.2% | 81.5% | 83.5% | 81.3% | 79.5% | 88.2% | 78.5% | 76.2% | 84.5% | 86.2% | 82.36% | 4.662%
24 hours | 99.9% | 100% | 100% | 99.8% | 99.9% | 99.9% | 100% | 100% | 100% | 99.9% | 99.94% | -0.04002%
HV Faults: Other 3 hours | 92.7% | 93.5% | 91.8% | 91% | 93.9% | 93.2% | 91.5% | 91.2% | 93% | 93.5% | 92.53%
24 hours | 99.9% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.99%
HV Faults: Total 3 hours | 91.7% | 92.8% | 90.9% | 91.6% | 91.7% | 93.1% | 90% | 90.2% | 93.3% | 92.1% | 91.74% | 0.3924%
24 hours | 99.9% | 100% | 100% | 100% | 99.9% | 100% | 100% | 100% | 100% | 100% | 99.98% | 0.02%
EHV Faults: 3 hours | 92.1% | 67.8% | 94.3% | 98.9% | 97.7% | 90.6% | 99.3% | 99.1% | 97.7% | 99.1% | 93.66% | 5.808%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
132kV F'lts: 3 hours | 100% | 100% | 100% | 98.7% | 100% | 100% | 100% | 100% | 100% | 100% | 99.87% | 0.1302%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
Total Faults:3 hours | 91.8% | 90.7% | 91.1% | 92.2% | 91.5% | 92.1% | 88.7% | 90.1% | 92.8% | 92.2% | 91.32% | 0.9636% | 92.8% | 88.7% |  | 1772970.042
24 hours | 99.9% | 100% | 100% | 100% | 99.9% | 100% | 100% | 100% | 100% | 100% | 99.98% | 0.02% | 100% | 99.9% |  | 1922961
TOTAL not rest in 3 hrs | 7.6% | 15.1% | 8.2% | 9.3% | 8.9% | 7.8% | 11.3% | 9.9% | 7.2% | 7.8% | 8.68% | -10.14% | 15.1% | 7.2% |  |  |  | 1 | 0
TOTAL not rest in 24 hrs | 0% | 1% | 0.1% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.02% | -100% | 1% | 0% |  |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- Load Disconnection | * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(b) due to plc action
- Voltage Reductions | * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- Load Disconnection | * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 1.51 | 1.1 | 1 | 0.6 | 0.78 | 0.61 | 2.58 | 1.02 | 1.47 | 1.06 | 1.173 | 10 | 2.58 | 0.6 |  |  |  | 1 | 0
* Overall reliability for 1991/2 affected by change in measured length of system
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
EME total distribution system | 13.7 | 13.6 | 13.8 | 12.96 | 16.9 | 14.63 | 20 | 16.95 | 13.4 | 12.5 | 14.844 | -5.1% | 20 | 12.5 |  |  |  | 1 | 1
5 RELEVANT DATA:
Number of Customers | 1930000 | 1938000 | 1952000 | 1968761 | 1977000 | 1985000 | 2071000 | 2108000 | 2126000 | 2139000
Embedded Gen.Stations | 1 | 1 | 1 | 1 | 1 | 37 | 50 | 61 | 73 | 76
Emb.Gen.Capacity MWSO | 342 | 342 | 342 | 342 | 342 | 248 | 257 | 260.93 | 326 | 330
[9 empty] | %age overhead all voltages | 27.26%
Mains in commission (circuit kilometres)
Overhead Line
132kV |  |  |  | 0 | 1179 | 1178 | 1178 | 1178 | 1178 | 1179
EHV |  |  |  | 0 | 1323 | 1322 | 1322 | 1321 | 1322 | 1321
25kV |  |  |  | 0
11kV |  |  |  | 0
6.6kV |  |  |  | 0
HV |  |  |  | 0 | 5657 | 5882 | 5882 | 5646 | 5624 | 5610
3kV |  |  |  | 0
0
0
0
LV |  |  |  | 0 | 4180 | 4283 | 4283 | 4165 | 4161 | 4156
TOTAL | [5 empty] | 12339 | 12665 | 12310 | 12285 | 12266
Underground cable
132kV |  |  |  | 0 | 333 | 333 | 333 | 333 | 333 | 333
EHV |  |  |  | 0 | 1239 | 1237 | 1237 | 1250 | 1250 | 1250
25kV |  |  |  | 0
11kV |  |  |  | 0
6.6kV |  |  |  | 0
HV |  |  |  | 0 | 10127 | 10323 | 10323 | 10659 | 10750 | 10870
3kV |  |  |  | 0
0
0
LV |  |  |  | 0 | 19761 | 20354 | 20354 | 20019 | 20155 | 20283
TOTAL | [6 empty] | 31460 | 32247 | 32488 | 32736
45002
Transformers
Primary Voltage
132kV | [6 empty] | 157 | 154 | 154 | 154
33kV | [6 empty] | 450 | 570 | 452 | 448
Distribution pole-mounted | [6 empty] | 12806 | 13490 | 13497 | 13519
Distribution Other | [6 empty] | 17752 | 17768 | 18169 | 18464
Capacity | [7 empty] | 31982 | 32272 | 32585
132kV | [6 empty] | 8369 | 8249 | 8262 | 8684
33kV | [6 empty] | 6844 | 6606 | 6663 | 6882
Distribution | [6 empty] | 8669 | 8886 | 8930 | 8930
[7 empty] | 23883 | 23741 | 23855 | 24496
HV O/H length (km) | 5983 | 5950 | 5917 | 5884 | 5851 | 5818 | 5785 | 5752 | 5752 | 5610
HV U/G length (km) | 10099.5356 | 10095.3033 | 10091.0711 | 10086.8389 | 10082.6067 | 10078.3744 | 10074.1422 | 10069.91 | 10750 | 10870
SECURITY : customer supply interruptions per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 4.0131 | 3.0715 | 3.8688 | 3.1229 | 6.2746 | 7.2874 | 9.8676 | 4.8147 | 6.1308 | 3.7388 | 5.219 |  | 9.8676 | 3.0715
HV faults: U/G damage | 78.7323 | 77.1721 | 84.5326 | 75.7303 | 89.4126 | 73.6617 | 67.2233 | 77.8732 | 88.2043 | 71.628 | 78.417 |  | 89.4126 | 67.2233
HV faults: O/H no damage | 26.4516 | 22.4743 | 31.0103 | 16.7298 | 30.0723 | 26.9534 | 22.9117 | 24.1878 | 20.3286 | 18.3016 | 23.9421 |  | 31.0103 | 16.7298
HV faults: O/H damage | 30 | 28.3371 | 33.3196 | 27.4368 | 34.8028 | 30.0241 | 34.0095 | 34.0828 | 39.1787 | 37.7471 | 32.8938 |  | 39.1787 | 27.4368
HV underground networks | 82.7454 | 80.2437 | 88.4013 | 78.8532 | 95.6872 | 80.9491 | 77.0909 | 82.6879 | 94.3351 | 75.3668 | 83.636 |  | 95.6872 | 75.3668 |  |  |  | 1 | 1
HV overhead networks | 56.4516 | 50.8114 | 64.3299 | 44.1666 | 64.8751 | 56.9775 | 56.9212 | 58.2705 | 59.5073 | 56.0487 | 56.836 |  | 64.8751 | 44.1666 |  |  |  | 1 | 0
Availability : customer minutes lost per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 248.4273 | 153.5764 | 290.1575 | 214.6993 | 411.7685 | 512.0866 | 698.9578 | 418.6731 | 375.7581 | 275.4922 | 359.9597 |  | 698.9578 | 153.5764
HV faults: U/G damage | 6306.2306 | 5413.5669 | 7002.4677 | 5855.4351 | 6784.3765 | 5357.2131 | 6146.7169 | 6782.5035 | 6407.6651 | 5923.0819 | 6197.9257 |  | 7002.4677 | 5357.2131
HV faults: O/H no damage | 2935.4839 | 2052 | 3925.7732 | 1606.0593 | 3683.0115 | 2456.5143 | 2470.1642 | 3151.7385 | 1848.0529 | 1868.2888 | 2599.7086 |  | 3925.7732 | 1606.0593
HV faults: O/H damage | 3419.3548 | 3289.7143 | 3694.8454 | 3145.1994 | 4392.5825 | 3002.4063 | 4797.1305 | 4617.6634 | 3991.7942 | 4155.9893 | 3850.668 |  | 4797.1305 | 3002.4063
HV underground networks | 6554.6578 | 5567.1433 | 7292.6253 | 6070.1343 | 7196.145 | 5869.2997 | 6845.6746 | 7201.1766 | 6783.4233 | 6198.5741 | 6557.8854 |  | 7292.6253 | 5567.1433 |  |  |  | 1 | 0
HV overhead networks | 6354.8387 | 5341.7143 | 7620.6186 | 4751.2587 | 8075.5939 | 5458.9206 | 7267.2947 | 7769.4019 | 5839.847 | 6024.2781 | 6450.3767 |  | 8075.5939 | 4751.2587 |  |  |  | 1 | 0
5625.25
5186.4805
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
| 2148090 | 1994395.8 | 3121248 | 1960885.956 | 2056080 | 1889720 | 1847332 | 1918280 | 2030330 | 1922961
| 215388000 | 186435600 | 230921600 | 165572800.1 | 184454100 | 154631500 | 184940300 | 194568400 | 161150800 | 156574800

## I
Southern
Year: | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 3.77 | 3.7 | 4.11 | 4.1 | 3.71 | 2.99 | 2.56 | 2.26 | 2.11 | 2.61 | 3.192
LV faults | 4.296 | 4.74 | 5.34 | 4.96 | 4.45 | 5.09 | 3.96 | 3.63 | 3.37 | 4.42 | 4.4256 | [8 empty] | 147710.2376
HV faults: U/G no damage | 0.32 | 0.49 | 0.42 | 0.13 | 0.25 | 0.66 | 0.33 | 0.55 | 0.23 | 0.66 | 0.404
HV faults: U/G damage | 21.55 | 20.64 | 22.74 | 20.29 | 21.05 | 22.98 | 22.27 | 20.61 | 22.08 | 23.46 | 21.767
HV faults: O/H no damage | 6.04 | 6.28 | 7.07 | 5.15 | 5.62 | 6.73 | 6.98 | 4.55 | 3.98 | 7.54 | 5.994
HV faults: O/H damage | 10.78 | 10.62 | 10.82 | 12.01 | 10.7 | 12.71 | 11.55 | 10.28 | 6.81 | 7.72 | 10.4 |  |  |  |  | 1980899.7208
HV faults: All other | 12.8405 | 11.98 | 11.05 | 11.98 | 13.48 | 16.34 | 16.84 | 13.8 | 13.72 | 13.65 | 13.568 |  |  |  |  | 2029718.25
HV faults: Total | 51.5305 | 50.01 | 52.1 | 49.56 | 51.1 | 59.42 | 57.97 | 49.79 | 46.82 | 53.03 | 52.133 | 1.721% |  |  |  | 2085361.2233 |  |  |  | 1397716.7074
EHV faults | 10.0891 | 7.49 | 9.87 | 8.93 | 8.09 | 5.7 | 6.62 | 7.63 | 5.98 | 9.7 | 8.0099 | 21.1% |  |  |  | 1994223.6072 |  |  |  | 214750.131
132kV faults | 1.9349 | 0.76 | 0.79 | 2.79 | 1.24 | 2.77 | 2.33 | 6.34 | 2.71 | 2.96 | 2.4625 | 20.2% |  |  |  | 1938143.5174 |  |  |  | 66020.6876
Total of (a) | 71.62 | 66.7 | 72.21 | 70.34 | 68.62 | 75.97 | 73.44 | 69.65 | 60.99 | 72.72 | 70.226 | 3.551% |  |  |  | 2061414.4166
(b) Planned Outages | 8.4559 | 10.67 | 8.81 | 7.87 | 6.69 | 3.33 | 2.91 | 1.93 | 1.83 | 1.65 | 5.4146 | -69.53% |  |  |  | 2072131.9776 |  |  |  | 145168.3033
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1925294.7413
(d) Other Systems | 0 | 3.9 | 1.47 | 0 | 0 | 0 | 2.67 | 1.15 | 1.15 | 0 | 1.034 |  |  |  |  | 1696745.3976 |  |  |  | 27722.1294
Total of (a+b+c+d) | 80.08 | 81.27 | 82.49 | 78.21 | 75.31 | 79.31 | 79.02 | 72.73 | 63.97 | 74.37 | 76.676 | -3.007% | 82.49 | 63.97 |  | 1993902.0909 | 81.3806 | 1 | 0 | 2055727.2653
[10 empty] | 72.72 | [5 empty] | 1949664.6504
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | 6.71 | 5.54 | 5.36 | 4.97 | 6.81 | 4.31 | 3.35 | 2.71 | 2.49 | 3.4 | 4.565
LV faults | 10.2506 | 10.95 | 11.46 | 10.73 | 11.4 | 12.34 | 9.37 | 8.43 | 8.35 | 11.38 | 10.4661 | [8 empty] | 34931814.8284
HV faults: U/G no damage | 0.3 | 0.36 | 0.22 | 0.11 | 0.14 | 0.41 | 0.2 | 0.21 | 0.11 | 0.41 | 0.247
HV faults: U/G damage | 22.53 | 20.56 | 19.88 | 17.14 | 18.62 | 19.35 | 17.3 | 14.46 | 15.62 | 15.56 | 18.102
HV faults: O/H no damage | 4.33 | 4.74 | 4.17 | 3.31 | 4.52 | 4.99 | 4.51 | 2.7 | 2.27 | 3.28 | 3.882
HV faults: O/H damage | 13.63 | 12.3 | 11.57 | 12.27 | 11.87 | 16.77 | 12.79 | 9.39 | 6.46 | 6.95 | 11.4 |  |  |  |  | 257210230.98
HV faults: All other | 10.6028 | 10.38 | 7.45 | 7.92 | 10.28 | 10.92 | 10.51 | 6.99 | 7.16 | 6.94 | 8.9153 |  |  |  |  | 272677050
HV faults: Total | 51.3928 | 48.34 | 43.29 | 40.75 | 45.43 | 52.44 | 45.31 | 33.75 | 31.62 | 33.14 | 42.5463 | -22.11% |  |  |  | 230807952.1 |  |  |  | 142003683.8145
EHV faults | 4.9633 | 3.1 | 5.71 | 3.44 | 2.98 | 2.38 | 2.85 | 2.61 | 3.97 | 4.13 | 3.6133 | 14.3% |  |  |  | 189707500.8 |  |  |  | 12059940.8801
132kV faults | 0.096744 | 0.61 | 0.02 | 0.11 | 0.01 | 0.22 | 0.14 | 3.43 | 0.11 | 1.2 | 0.59467 | 101.8% |  |  |  | 199733525.94 |  |  |  | 1984802.4026
Total of (a) | 73.41 | 68.54 | 65.84 | 60 | 66.68 | 71.69 | 61.02 | 50.93 | 46.54 | 53.25 | 61.79 | -13.82% |  |  |  | 202684524.28
(b) Planned Outages | 30.5682 | 39.37 | 24.3 | 14.4 | 10.92 | 6.29 | 6.05 | 4.77 | 4.74 | 4.29 | 14.5698 | -70.56% |  |  |  | 176296422.24 |  |  |  | 48628648.6163
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 148321551.43
(d) Other Systems | 0 | 1.27 | 1.16 | 0 | 0 | 0 | 0.16 | 0.33 | 0.35 | 0 | 0.327 |  |  |  |  | 136943825.04 |  |  |  | 1091404.683
Total of (a+b+c+d) | 103.98 | 109.18 | 91.3 | 74.4 | 77.61 | 77.98 | 67.23 | 56.03 | 51.63 | 57.54 | 76.688 | -24.97% | 109.18 | 51.63 |  | 154268019.78 | 70.7944 | 1 | 0 | 255956092.752
[10 empty] | 53.25 | [5 empty] | 142766285.25
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 57.83% | 57.17% | 70.13% | 71.24% | 60.91% | 63.16% | 63.46% | 66.89% | 65.35% | 62.79% | 63.89% | -1.726%
24 hours | 99.31% | 99.65% | 99.79% | 99.82% | 99.78% | 99.97% | 100% | 99.99% | 100% | 99.98% | 99.83% | 0.1512%
HV Faults:U/G no damage 3 hours | 99.3% | 94.23% | 99.13% | 89.51% | 98.88% | 97.28% | 99.67% | 100% | 100% | 91.49% | 96.95% | -5.631%
24 hours | 99.97% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.003%
HV Faults: U/G damage 3 hours | 92.51% | 91.94% | 94.42% | 94.81% | 94.76% | 94.54% | 95.31% | 96.17% | 95.9% | 96.1% | 94.65% | 1.536%
24 hours | 99.91% | 99.96% | 99.97% | 99.94% | 99.96% | 100% | 100% | 100% | 100% | 100% | 99.97% | 0.02601%
HV Faults: O/H no damage 3 hours | 92.64% | 92.85% | 96.84% | 95.88% | 93.5% | 93.75% | 93.42% | 96.5% | 94.84% | 97.35% | 94.76% | 2.736%
24 hours | 100% | 100% | 100% | 100% | 100% | 99.93% | 100% | 100% | 100% | 100% | 99.99% | 0.007%
HV Faults: O/H damage 3 hours | 80.68% | 84.99% | 84.35% | 86.07% | 84.04% | 82.55% | 84.74% | 89.93% | 87.5% | 89.23% | 85.41% | 4.475%
24 hours | 100% | 99.96% | 99.99% | 100% | 99.95% | 99.75% | 100% | 99.97% | 100% | 100% | 99.96% | 0.03801%
HV Faults: Other 3 hours | [10 empty] | #DIV/0!
24 hours | [10 empty] | #DIV/0!
HV Faults: Total 3 hours | 89.95% | 90.46% | 92.67% | 92.85% | 92.26% | 92.07% | 92.99% | 94.94% | 94.59% | 94.99% | 92.78% | 2.385%
24 hours | 99.96% | 99.96% | 99.98% | 99.97% | 99.97% | 99.94% | 100% | 99.99% | 100% | 100% | 99.98% | 0.02304%
EHV Faults: 3 hours | 96.19% | 98.31% | 92.39% | 99.37% | 97.53% | 96.88% | 98.43% | 99.77% | 94.3% | 95.43% | 96.86% | -1.477%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 4.007e-05%
132kV F'lts: 3 hours | 100% | 85.68% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.57% | 1.453%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
Total Faults:3 hours | 89.13% | 88.83% | 90% | 91.22% | 89.37% | 89.8% | 91.64% | 93.7% | 92.35% | 92.17% | 90.82% | 1.485% | 93.7% | 88.83% |  | 1837779.5572
24 hours | 99.93% | 99.94% | 99.96% | 99.97% | 99.95% | 99.95% | 100% | 99.99% | 100% | 100% | 99.97% | 0.03145% | 100% | 99.93% |  | 1993902.0909
TOTAL not rest in 3 hrs | 10.87% | 11.17% | 10% | 8.78% | 10.63% | 10.2% | 8.36% | 6.3% | 7.65% | 7.83% | 9.179% | -14.69% | 11.17% | 6.3% |  |  |  | 1 | 0
TOTAL not rest in 24 hrs | 0.07436% | 0.06% | 0.04% | 0.03% | 0.05% | 0.05% | 0% | 0.01% | 0% | 0% | 0.03144% | -100% | 0.07436% | 0% |  |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At NGC request* | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
*No. of occasions upto and including1990/91. | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
Demand in MWh lost per 100 customers thereafter | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
TOTAL | N/A | N/A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | N/A | N/A
(b) due to plc action | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*No. of occasions upto and including1990/91. | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
Demand in MWh lost per 100 customers thereafter | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
Total* | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 1.1521 | 2.36 | 1.74 | 2.73 | 2.31 | 2.32 | 1.51 | 1.19 | 1.05 | 1.53 | 1.7892 | 10 | 2.73 | 1.05 |  |  |  | 1 | 0
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
Excluding service faults# | 12.2129 | 12.01 | 14.85 | 13.64 | 13.74 | 13.16 | 11.74 | 12.38 | 12.12 | 13.57 | 12.9423 | 4.85% | 14.85 | 11.74 |  |  |  | 0 | 0
5 RELEVANT DATA: | [11 empty] | 7.865%
Number of Customers | 2473651 | 2497500 | 2528017 | 2549832 | 2573554 | 2599186 | 2622288 | 2647181 | 2652408 | 2681057 |  | 4.339%
Embedded Gen.Stations | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 4 | N/A | N/A
Emb.Gen.Capacity MWSO | 588 | 588 | 588 | 588 | 308 | 308 | 308 | 308 | 308 | 474 | N/A | N/A
NOTES N/A - Information not applicable |  |  | * - Information not available |  |  | # - Nine year average |  |  | %age overhead all voltages | 38.26%
Mains in commission (circuit kilometres)
Overhead Line
132kV | 1981 | 1981 | 1981 | 1981 | 1981 | 1981 | 1981 | 1894 | 1900 | 1920
66kV | [5 empty] | 6 | 6 | 6 | 6 | 6
33kV | 3440 | 3392 | 3605 | 3604 | 3604 | 3612 | 3610 | 3503 | 3552 | 3465
25kV
22kV | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 7 | 7 | 7
11kV | 14319 | 14344 | 14360 | 14380 | 14388 | 14381 | 14331 | 13597 | 13347 | 13400
6.6kV | 102 | 98 | 95 | 93 | 93 | 93 | 91 | 63 | 60 | 60
2kV to 3.3kV | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 5 | 3 | 2
LV | 8868 | 8860 | 8852 | 8836 | 8836 | 8836 | 8828 | 9038 | 9038 | 8968
TOTAL | 28734 | 28699 | 28917 | 28918 | 28926 | 28933 | 28870 | 28113 | 27913 | 27828
Underground cable
132kV | 313 | 313 | 321 | 321 | 321 | 321 | 322 | 366 | 392 | 387
66kV | 198 | 198 | 200 | 201 | 201 | 179 | 184 | 141 | 165 | 148
33kV | 1086 | 1093 | 1098 | 1101 | 1103 | 1103 | 1107 | 1228 | 1234 | 1332
25kV |  |  |  |  | 5
22kV | 485 | 484 | 485 | 484 | 480 | 480 | 469 | 366 | 354 | 358
11kV | 11317 | 11453 | 11622 | 11779 | 11807 | 11898 | 12244 | 12479 | 12731 | 13121
6.6kV | 1485 | 1488 | 1492 | 1482 | 1478 | 1478 | 1482 | 632 | 629 | 647
2kV to 3.3kV | 388 | 383 | 376 | 368 | 368 | 368 | 343 | 146 | 124 | 121
LV | 25974 | 26147 | 26437 | 26644 | 26736 | 26890 | 27224 | 27984 | 28392 | 28798
TOTAL | 41246 | 41559 | 42031 | 42380 | 42499 | 42717 | 43375 | 43342 | 44021 | 44912
72740
Transformers
Primary Voltage
132kV | [7 empty] | 231 | 231 | 234
33kV | [7 empty] | 859 | 862 | 864
Distribution pole-mounted | [7 empty] | 25483 | 25477 | 25629
Distribution Other | [7 empty] | 25966 | 24889 | 26486
Capacity | [7 empty] | 52539 | 51429 | 53213
132kV | [7 empty] | 14538 | 14515 | 14359
33kV | [7 empty] | 14669 | 14552 | 14853
Distribution | [7 empty] | 13537.1 | 13106.6 | 13521.5
[8 empty] | 42744.1 | 42173.6 | 42733.5
HV O/H length (km) | 14432 | 14453 | 14466 | 14484 | 14492 | 14485 | 14432 | 13665 | 13410 | 13462
HV U/G length (km) | 13190 | 13324 | 13490 | 13629 | 13653 | 13744 | 14069 | 13257 | 13484 | 13889
SECURITY : customer supply interruptions per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 0.60013 | 0.91847 | 0.78708 | 0.24322 | 0.47124 | 1.2482 | 0.61508 | 1.0982 | 0.45243 | 1.274 | 0.77081 |  | 1.274 | 0.24322
HV faults: U/G damage | 40.4148 | 38.6884 | 42.6146 | 37.9603 | 39.6787 | 43.4585 | 41.5085 | 41.1544 | 43.4331 | 45.2859 | 41.4197 |  | 45.2859 | 37.9603
HV faults: O/H no damage | 10.3526 | 10.8519 | 12.3552 | 9.0663 | 9.9802 | 12.0763 | 12.6826 | 8.8143 | 7.8722 | 15.0165 | 10.9068 |  | 15.0165 | 7.8722
HV faults: O/H damage | 18.477 | 18.3515 | 18.9086 | 21.143 | 19.0015 | 22.8068 | 20.9863 | 19.9144 | 13.4697 | 15.375 | 18.8434 |  | 22.8068 | 13.4697
HV underground networks | 41.015 | 39.6069 | 43.4017 | 38.2035 | 40.1499 | 44.7066 | 42.1236 | 42.2527 | 43.8855 | 46.5599 | 42.1905 |  | 46.5599 | 38.2035 |  |  |  | 0 | 0
HV overhead networks | 28.8296 | 29.2035 | 31.2638 | 30.2093 | 28.9818 | 34.8831 | 33.6689 | 28.7286 | 21.3419 | 30.3914 | 29.7502 |  | 34.8831 | 21.3419 |  |  |  | 0 | 0
Availability : customer minutes lost per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 56.262 | 67.4797 | 41.2279 | 20.5798 | 26.3896 | 77.5368 | 37.2775 | 41.9332 | 21.6379 | 79.1442 | 46.9468 |  | 79.1442 | 20.5798
HV faults: U/G damage | 4225.2735 | 3853.8427 | 3725.4987 | 3206.7005 | 3509.8202 | 3659.3604 | 3224.5065 | 2887.3981 | 3072.5759 | 3003.6177 | 3436.8594 |  | 4225.2735 | 2887.3981
HV faults: O/H no damage | 742.1639 | 819.0791 | 728.7316 | 582.7081 | 802.6818 | 895.4048 | 819.465 | 523.0434 | 448.9908 | 653.2363 | 701.5505 |  | 895.4048 | 448.9908
HV faults: O/H damage | 2336.1879 | 2125.4584 | 2021.9243 | 2160.0689 | 2107.9275 | 3009.206 | 2323.9373 | 1819.0289 | 1277.7446 | 1384.144 | 2056.5628 |  | 3009.206 | 1277.7446
HV underground networks | 4281.5354 | 3921.3224 | 3766.7266 | 3227.2802 | 3536.2098 | 3736.8972 | 3261.7841 | 2929.3313 | 3094.2137 | 3082.7619 | 3483.8063 |  | 4281.5354 | 2929.3313 |  |  |  | 1 | 0
HV overhead networks | 3078.3517 | 2944.5375 | 2750.6559 | 2742.777 | 2910.6093 | 3904.6108 | 3143.4023 | 2342.0723 | 1726.7354 | 2037.3803 | 2758.1132 |  | 3904.6108 | 1726.7354 |  |  |  | 1 | 0
9870.818
9097.933
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
| 1980899.7208 | 2029718.25 | 2085361.2233 | 1994223.6072 | 1938143.5174 | 2061414.4166 | 2072131.9776 | 1925294.7413 | 1696745.3976 | 1993902.0909
| 257210230.98 | 272677050 | 230807952.1 | 189707500.8 | 199733525.94 | 202684524.28 | 176296422.24 | 148321551.43 | 136943825.04 | 154268019.78

## J
SWALEC
Year: | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 1.5134 | 1.2689 | 0.51214 | 0.6 | 0.5 | 0.3 | 0.4 | 0.5 | 0.7 | 0.5 | 0.67944
LV faults | 9.4004 | 7.881 | 4.1 | 4.1 | 3.5 | 2.4 | 3.3 | 3.1 | 3.5 | 3.6 | 4.4881 | [8 empty] | 149797.698
HV faults: U/G no damage | 2.4786 | 1.0828 | 1.6689 | 1.3 | 1.6 | 2.8 | 4.2 | 0.9 | 2.4 | 1.5 | 1.993
HV faults: U/G damage | 52.0686 | 47.8439 | 59.2444 | 59.9 | 62.3 | 46.7 | 47 | 44.3 | 36.8 | 36.6 | 49.2757
HV faults: O/H no damage | 16.2505 | 10.0233 | 10.7154 | 12.9 | 17.6 | 15.7 | 14.3 | 18.5 | 20.8 | 23.2 | 15.9989
HV faults: O/H damage | 33.5017 | 29.16 | 26.0832 | 35.3 | 27.5 | 38 | 28 | 26.6 | 23.4 | 21.1 | 28.8645 |  |  |  |  | 2609389.252
HV faults: All other | 69.7363 | 41.4945 | 32.2513 | 35.1 | 31.4 | 31.5 | 29.2 | 30.6 | 16.5 | 16 | 33.3782 |  |  |  |  | 2115545.796
HV faults: Total | 174.0357 | 129.6045 | 129.9633 | 144.6 | 140.4 | 134.7 | 122.8 | 120.9 | 99.9 | 98.4 | 129.5303 | -24.03% |  |  |  | 1825729.543 |  |  |  | 1280666.509
EHV faults | 14.0783 | 13.8443 | 11.4253 | 15.8 | 17.7 | 27.5 | 17.1 | 17.9 | 11.2 | 9.8 | 15.6348 | -37.32% |  |  |  | 2024396.325 |  |  |  | 154581.2545
132kV faults | 0 | 0.92631 | 14.9093 | 7 | 19.1 | 17.2 | 5.1 | 1.4 | 2.2 | 16.4 | 8.4236 | 94.69% |  |  |  | 2101430.5 |  |  |  | 83283.7423
Total of (a) | 197.5 | 152.3 | 160.3846 | 171.5 | 180.6 | 181.9 | 148.3 | 143.3 | 116.8 | 128.3 | 158.0885 | -18.84% |  |  |  | 2152165.4
(b) Planned Outages | 80 | 75.7 | 34.9 | 42 | 38.9 | 41.2 | 43.4 | 42.4 | 33.4 | 17.1 | 44.9 | -61.92% |  |  |  | 1858723.2 |  |  |  | 443926.3
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0.04 |  |  |  |  | 1813546.2
(d) Other Systems | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 1.29 |  |  |  |  | 1473762.4 |  |  |  | 13149.71
Total of (a+b+c+d) | 284.6 | 229.2 | 195.2846 | 213.5 | 219.7 | 223.3 | 191.7 | 185.7 | 150.2 | 152.7 | 204.5885 | -25.36% | 284.6 | 150.2 |  | 1509744.9 | 81.3806 | 1 | 0 | 2022766.1196
[10 empty] | 135.6 | [5 empty] | 1340677.2
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | * | * | 0.91838 | 1.1 | 0.8 | 0.6 | 0.8 | 0.8 | 0.9 | 1.2 | 0.71184
LV faults | 17.6 | 17.2 | 8.9 | 7.9 | 6.9 | 5.2 | 6.6 | 8.2 | 4.7 | 5.5 | 8.87 | [8 empty] | 29604765.1529
HV faults: U/G no damage | 2.1 | 0.7 | 1.1 | 0.8 | 0.9 | 1.3 | 3.8 | 0.5 | 1.6 | 1.3 | 1.41
HV faults: U/G damage | 52.6 | 44.5 | 52.1 | 52.3 | 58 | 46.5 | 45.1 | 41.2 | 33.6 | 33.3 | 45.92
HV faults: O/H no damage | 11.6 | 6.9 | 9.2 | 10.7 | 16.6 | 17.8 | 12.4 | 14.2 | 17.3 | 16.2 | 13.29
HV faults: O/H damage | 39.5 | 32.8 | 28.2 | 46.8 | 38.8 | 72.2 | 35.3 | 34.2 | 25.1 | 22 | 37.49 |  |  |  |  | 302632108.8
HV faults: All other | 37.8 | 27 | 24.7 | 28.4 | 25.6 | 26.2 | 23.7 | 22.8 | 14.1 | 11.4 | 24.17 |  |  |  |  | 300329362.17
HV faults: Total | 143.601 | 112.0313 | 115.2781 | 139 | 140 | 164.2 | 120.3 | 112.9 | 91.7 | 84.2 | 122.321 | -31.16% |  |  |  | 198512099.2 |  |  |  | 408262243.7831
EHV faults | 12.2728 | 3.7811 | 3.5554 | 6.3 | 8.2 | 10.5 | 9.6 | 10.1 | 6.8 | 3.2 | 7.4309 | -56.94% |  |  |  | 189164902.5 |  |  |  | 24801657.6564
132kV faults | 0 | 0.10189 | 6.9655 | 2.4 | 4.6 | 8.9 | 0.5 | 1 | 0.6 | 12.3 | 3.7367 | 229.2% |  |  |  | 202778000 |  |  |  | 12471863.8568
Total of (a) | 173.4738 | 133.0893 | 134.7335 | 155.6 | 159.6 | 188.7 | 137 | 132.2 | 103.8 | 106.6 | 142.4797 | -25.18% |  |  |  | 224276260
(b) Planned Outages | 155.5 | 192.29 | 77.6 | 43.9 | 52.3 | 43.8 | 52.3 | 50.7 | 41.4 | 18 | 72.779 | -75.27% |  |  |  | 183545280 |  |  |  | 242909300.991
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0.02 |  |  |  |  | 178620140
(d) Other Systems | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2 | 1.33 |  |  |  |  | 142470240 |  |  |  | 4505799.15
Total of (a+b+c+d) | 330.0738 | 325.3793 | 212.3335 | 199.5 | 212 | 232.7 | 189.3 | 182.9 | 145.2 | 136.8 | 216.6187 | -36.85% | 330.0738 | 136.8 |  | 135254160 | 70.7944 | 1 | 1 | 722992738.2026
Note: * indicates information either not available or inapplicable | [9 empty] | 118.8 | [5 empty] | 117457560
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 56.9% | 47.6% | 50.01% | 56.38% | 55.67% | 50.49% | 56.84% | 53.9% | 55.7% | 62.4% | 54.59% | 14.31%
24 hours | 99.9% | 99.76% | 99.97% | 99.78% | 99.84% | 99.76% | 99.92% | 94.7% | 99.8% | 100% | 99.34% | 0.6599%
HV Faults:U/G no damage 3 hours | 91.68% | 96.35% | 98.37% | 98.14% | 98.61% | 98.29% | 84.91% | 100% | 98.7% | 84.4% | 94.94% | -11.11%
24 hours | 99.64% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.96% | 0.0361%
HV Faults: U/G damage 3 hours | 88.95% | 91.25% | 93.07% | 92.63% | 91.2% | 89.67% | 91.31% | 92.6% | 90.5% | 92.7% | 91.39% | 1.437%
24 hours | 99.93% | 100% | 100% | 100% | 99.97% | 100% | 100% | 100% | 100% | 100% | 99.99% | 0.009999%
HV Faults: O/H no damage 3 hours | 91.16% | 92.87% | 90.3% | 89.9% | 90.84% | 87.32% | 89.5% | 90.9% | 91.8% | 93.9% | 90.85% | 3.357%
24 hours | 100% | 100% | 100% | 100% | 99.72% | 99.38% | 99.99% | 100% | 100% | 100% | 99.91% | 0.09138%
HV Faults: O/H damage 3 hours | 84.1% | 84.18% | 86.92% | 79.77% | 81.11% | 75.32% | 78.6% | 76.5% | 84.8% | 84.8% | 81.61% | 3.91%
24 hours | 99.75% | 100% | 100% | 99.89% | 99.94% | 98.34% | 99.98% | 99.9% | 100% | 100% | 99.78% | 0.2207%
HV Faults: Other 3 hours | 94.24% | 93.42% | 91.52% | 91.99% | 90.06% | 89.82% | 92.17% | 92.7% | 89.4% | 91.2% | 91.65%
24 hours | 99.95% | 100% | 99.98% | 100% | 99.98% | 100% | 100% | 100% | 100% | 100% | 99.99%
HV Faults: Total 3 hours | 90.38% | 90.52% | 91.29% | 89.14% | 89.01% | 85.56% | 88.18% | 88.9% | 89.5% | 90.9% | 89.34% | 1.749%
24 hours | 99.91% | 100% | 100% | 99.97% | 99.93% | 99.46% | 100% | 100% | 100% | 100% | 99.93% | 0.07358%
EHV Faults: 3 hours | 88.16% | 99.62% | 100% | 97.22% | 93.56% | 99.65% | 93.07% | 87.8% | 95.3% | 98.8% | 95.32% | 3.653%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
132kV F'lts: 3 hours | n/a | 100% | 93.13% | 100% | 100% | 86.09% | 100% | 100% | 100% | 100% | 87.92% | 13.74%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
Total Faults:3 hours | 88.63% | 89.18% | 91.02% | 89.55% | 89.97% | 87.28% | 88.47% | 88.1% | 89.2% | 91.6% | 89.3% | 2.576% | 91.6% | 87.28% |  | 1382926.3284
24 hours | 99.91% | 99.99% | 100% | 99.97% | 99.94% | 99.59% | 99.99% | 99.9% | 100% | 100% | 99.93% | 0.071% | 100% | 99.59% |  | 1509744.9
TOTAL not rest in 3 hrs | 11.37% | 10.82% | 8.984% | 10.45% | 10.03% | 12.72% | 11.53% | 11.9% | 10.8% | 8.4% | 10.7% | -21.5% | 12.72% | 8.4% |  |  |  | 1 | 1
TOTAL not rest in 24 hrs | 0.08769% | 0.0143% | 0.004467% | 0.028% | 0.055% | 0.41% | 0.01% | 0.1% | 0% | 0% | 0.07095% | -100% | 0.41% | 0% |  |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | * | * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
- Load Disconnection | * | * | nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
(b) due to plc action
- Voltage Reductions | * | * | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
- Load Disconnection | * | * | nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 4.6 | 3.7 | 2.0537 | 1.2 | 1.9 | 2.2 | 1 | 1 | 0.9 | 0.7 | 1.9254 | 10 | 4.6 | 0.7 |  |  |  | 1 | 1
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
SWaE total system | 23.1034 | 21.6036 | 21.3981 | 18.5 | 17.53 | 15.95 | 16.51 | 16.12 | 15.07 | 14.15 | 17.9935 | 0.375% | 23.1034 | 14.15 |  |  |  | 1 | 1
5 RELEVANT DATA: | [7 empty] | Restated to exclude services | Restated to exclude services
Number of Customers | 916862 | 923013 | 934907 | 948195 | 956500 | 963800 | 969600 | 976600 | 981200 | 988700
Embedded Gen.Stations | * | * | * | * | 3 | * | * | * | * | 1
Emb.Gen.Capacity MWSO | * | * | * | * | 621 | * | * | * | * | 240
Note: * indicates information either not available or inapplicable | [8 empty] | %age overhead all voltages | 56.51%
Mains in commission (circuit kilometres)
Overhead Line
132kV |  | 1123 | 1124 | 1136 | 1144 | 1149 | 1149 | 1157 | 1165 | 1165
66 & 33kV |  | 1856 | 1800 | 1805 | 1814 | 1809 | 1812 | 1800 | 1800 | 1799
33kV |  |  |  |  | 1357
25kV |  |  |  |  | 1
22kV
11kV | 12475 | 12654 | 12475 | 12147 | 12297 | 12282 | 12282 | 12316 | 12316 | 12316
6.6kV |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LV |  | 3397 | 3389 | 3393 | 3375 | 3373 | 3378 | 3378 | 3378 | 3378
TOTAL |  | 19030 | 18788 | 18481 | 18630 | 18613 | 18621 | 18651 | 18659 | 18658
Underground cable
132kV |  | 67 | 67 | 60 | 60 | 68 | 68 | 69 | 69 | 71
66 & 33kV |  | 364 | 357 | 358 | 359 | 361 | 363 | 379 | 391 | 392
33kV
25kV |  |  |  |  | 236
22kV
11kV |  | 4513 | 4160 | 4171 | 4265 | 4432 | 4432 | 4619 | 4803 | 4863
6.6kV |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
3.3kV
3kV
LV |  | 8205 | 8275 | 8363 | 8441 | 8504 | 8627 | 8787 | 8927 | 9007
TOTAL |  | 13173 | 12883 | 12976 | 13149 | 13389 | 13514 | 13878 | 14214 | 14357
|  |  | 31671 | 31457 | 31779 | 32002 | 32135 | 32529 | 32873 | 33015
Transformers in commission |  |  |  | 29150
Not pole mounted | [5 empty] | 58351
132kV |  | 86 | 90 | 91 | 95 | 105 | 109 | 112 | 114 | 118
66kV or 33kV |  | 296 | 304 | 302 | 300 | 292 | 290 | 286 | 279 | 277
11kV and 6.6kV |  | 6940 | 7011 | 7052 | 7138 | 7180 | 7238 | 7287 | 7337 | 7425
TOTAL |  | 7322 | 7405 | 7445 | 7533 | 7577 | 7637 | 7685 | 7730 | 7820
33kV
Pole mounted
132kV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66kV or 33kV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11kV and 6.6kV |  | 30733 | 30944 | 31073 | 31164 | 31158 | 31139 | 31046 | 30888 | 30935
TOTAL |  | 30733 | 30944 | 31073 | 31164 | 31158 | 31139 | 31046 | 30888 | 30935
38755
Aggregate Capacity (MVA)
132kV |  | 4700 | 4740 | 4820 | 4860 | 5000 | 5090 | 5100 | 5065 | 5170
66kV or 33kV |  | 2658 | 2676 | 2719 | 2736 | 2817 | 2866 | 2877 | 2835 | 2827
11kV and 6.6kV |  | 3699 | 3819 | 3898 | 3938 | 3994 | 4057 | 4105 | 4362 | 4390
TOTAL |  | 11057 | 11235 | 11437 | 11534 | 11811 | 12013 | 12082 | 12262 | 12387
HV O/H length (km) | 12475 | 12654 | 12475 | 12147 | 12297 | 12282 | 12282 | 12316 | 12282 | 12316
HV U/G length (km) | 7283 | 7283 | 7283 | 7283 | 7283 | 7283 | 4456 | 4643 | 4827 | 4887
SECURITY : customer supply interruptions per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 3.1203 | 1.3722 | 2.1424 | 1.6925 | 2.1013 | 3.7054 | 9.139 | 1.893 | 4.8786 | 3.0347 | 3.3079 |  | 9.139 | 1.3722
HV faults: U/G damage | 65.5495 | 60.635 | 76.0511 | 77.9856 | 81.8206 | 61.8007 | 102.2693 | 93.1798 | 74.8046 | 74.0463 | 76.8142 |  | 102.2693 | 60.635
HV faults: O/H no damage | 11.9435 | 7.3112 | 8.0304 | 10.0697 | 13.6898 | 12.3202 | 11.2891 | 14.6696 | 16.617 | 18.6244 | 12.4565 |  | 18.6244 | 7.3112 |  |  |  | 0 | 0
HV faults: O/H damage | 24.6224 | 21.27 | 19.5474 | 27.5552 | 21.3904 | 29.8196 | 22.1045 | 21.0925 | 18.6941 | 16.9386 | 22.3035 |  | 29.8196 | 16.9386 |  |  |  | 1 | 1
Security - HV underground networks | 68.6698 | 62.0073 | 78.1935 | 79.6781 | 83.9219 | 65.5061 | 111.4083 | 95.0728 | 79.6831 | 77.081 | 80.1222 |  | 111.4083 | 62.0073
Security - HV overhead networks | 36.5659 | 28.5812 | 27.5778 | 37.6249 | 35.0802 | 42.1398 | 33.3936 | 35.7621 | 35.3111 | 35.563 | 34.76 |  | 42.1398 | 27.5778
Availability : customer minutes lost per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 264.3705 | 88.7147 | 141.2052 | 104.1543 | 118.1999 | 172.0362 | 826.8582 | 105.1691 | 325.2372 | 263.0059 | 240.8951 |  | 826.8582 | 88.7147
HV faults: U/G damage | 6621.8511 | 5639.7197 | 6687.9932 | 6809.0895 | 7617.328 | 6153.6043 | 9813.5009 | 8665.9315 | 6829.9814 | 6736.9982 | 7157.5998 |  | 9813.5009 | 5639.7197
HV faults: O/H no damage | 852.553 | 503.3025 | 689.4705 | 835.2422 | 1291.2011 | 1396.8116 | 978.9155 | 1125.9922 | 1382.0844 | 1300.4985 | 1035.6071 |  | 1396.8116 | 503.3025 |  |  |  | 0 | 0
HV faults: O/H damage | 2903.0901 | 2392.5104 | 2113.3769 | 3653.2087 | 3017.9881 | 5665.7189 | 2786.7513 | 2711.8967 | 2005.2206 | 1766.1091 | 2901.5871 |  | 5665.7189 | 1766.1091 |  |  |  | 1 | 1
Availability - HV underground networks | 6886.2215 | 5728.4344 | 6829.1985 | 6913.2438 | 7735.5279 | 6325.6405 | 10640.3591 | 8771.1006 | 7155.2186 | 7000.0041 | 7398.4949 |  | 10640.3591 | 5728.4344
Availability - HV overhead networks | 3755.6431 | 2895.8129 | 2802.8474 | 4488.4509 | 4309.1892 | 7062.5305 | 3765.6668 | 3837.8889 | 3387.305 | 3066.6077 | 3937.1942 |  | 7062.5305 | 2802.8474
16.697
15.2945
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
| 2609389.252 | 2115545.796 | 1825729.543 | 2024396.325 | 2101430.5 | 2152165.4 | 1858723.2 | 1813546.2 | 1473762.4 | 1509744.9
| 302632108.8 | 300329362.17 | 198512099.2 | 189164902.5 | 202778000 | 224276260 | 183545280 | 178620140 | 142470240 | 135254160

## K
South Western
Year: | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 2.3 | 2.1 | 2.6 | 1.6 | 1.3 | 1.4 | 1.1 | 1.1 | 1 | 1 | 1.55
LV faults | 6.8 | 7.1 | 5.3 | 5.5 | 5.3 | 5.3 | 4.8 | 4.4 | 4 | 3.7 | 5.22 | [8 empty] | 174224.2338
HV faults: U/G no damage | 0.9 | 1.3 | 1.2 | 1.3 | 0.6 | 1.4 | 1.3 | 1 | 1.1 | 2.3 | 1.24
HV faults: U/G damage | 27.7 | 25.5 | 26.4 | 22.2 | 24.5 | 22.9 | 22.7 | 18.1 | 16.9 | 15.5 | 22.24
HV faults: O/H no damage | 5.1 | 6.7 | 5.4 | 10.3 | 7.6 | 7.1 | 7 | 7.4 | 7.6 | 9.3 | 7.35
HV faults: O/H damage | 23.4 | 22.3 | 18.9 | 25.3 | 20 | 18.3 | 18.1 | 32.8 | 15.4 | 16.2 | 21.07 |  |  |  |  | 1818733.68
HV faults: All other | 31.7 | 19 | 22.6 | 20.1 | 19.7 | 22.9 | 16.2 | 14.7 | 12 | 13 | 19.19 |  |  |  |  | 1613859.77
HV faults: Total | 88.8 | 74.8 | 74.5 | 79.2 | 72.4 | 72.6 | 65.3 | 74 | 53 | 56.3 | 71.09 | -20.8% |  |  |  | 1499123.626 |  |  |  | 955449.6
EHV faults | 8.3 | 15.8 | 17.3 | 16 | 12.2 | 16.1 | 18 | 17 | 13.1 | 23.8 | 15.76 | 51.02% |  |  |  | 1525041.276 |  |  |  | 211814.4
132kV faults | 4.7 | 1.3 | 0 | 0.6 | 14 | 8 | 0 | 1 | 2.7 | 0 | 3.23 | -100% |  |  |  | 1597071 |  |  |  | 43411.2
Total of (a) | 110.9 | 101.1 | 99.7 | 102.9 | 105.2 | 103.4 | 89.2 | 97.5 | 73.8 | 84.9 | 96.86 | -12.35% |  |  |  | 1507114
(b) Planned Outages | 35.1 | 27.4 | 18.6 | 16.5 | 18.7 | 12.8 | 16.3 | 8 | 6.3 | 5.5 | 16.52 | -66.71% |  |  |  | 1379940 |  |  |  | 222028.8
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1395765
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1076544 |  |  |  | 0
Total of (a+b+c+d) | 146 | 128.5 | 118.3 | 119.4 | 123.9 | 116.2 | 105.5 | 105.5 | 80.1 | 90.4 | 113.38 | -20.27% | 146 | 80.1 | 99.9 | 1214976 | 81.3806 | 1 | 0 | 1523827.2
[10 empty] | 84.9 | [5 empty] | 1141056
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
#DIV/0!
LV faults | 15.9 | 15.8 | 14.6 | 14.8 | 12.7 | 13.1 | 12.9 | 12.3 | 9.4 | 9.2 | 13.07 | [8 empty] | 43622811.03
HV faults: U/G no damage | 0.6 | 0.8 | 1.3 | 1.2 | 0.5 | 1 | 1 | 0.7 | 0.6 | 1.4 | 0.91
HV faults: U/G damage | 27 | 29 | 28.4 | 22.7 | 21.9 | 18.3 | 18.2 | 13.3 | 9.8 | 9.8 | 19.84
HV faults: O/H no damage | 3.9 | 4.9 | 5 | 12.1 | 6.8 | 6.7 | 6.7 | 4.2 | 3.5 | 4.7 | 5.85
HV faults: O/H damage | 29.9 | 27 | 26 | 38 | 24.5 | 19.8 | 19.6 | 49 | 12.8 | 14 | 26.06 |  |  |  |  | 230705121.6
HV faults: All other | 21.2 | 16.2 | 20.3 | 17.7 | 11.6 | 16.7 | 10.2 | 8.4 | 6 | 7.3 | 13.56 |  |  |  |  | 221042272
HV faults: Total | 82.6 | 77.9 | 81 | 91.7 | 65.3 | 62.5 | 55.7 | 75.6 | 32.7 | 37.2 | 66.22 | -43.82% |  |  |  | 232661959.2 |  |  |  | 221017792.38
EHV faults | 5.7 | 6.8 | 24.4 | 6.7 | 3.8 | 8.3 | 6.9 | 4.7 | 3.3 | 6 | 7.66 | -21.67% |  |  |  | 213429143.4 |  |  |  | 25566238.14
132kV faults | 0.5 | 0.3 | 0 | 0.1 | 12.2 | 1 | 0 | 0.5 | 0.2 | 0 | 1.48 | -100% |  |  |  | 171565900 |  |  |  | 4939690.92
Total of (a) | 104.7 | 100.8 | 120 | 113.3 | 94 | 84.9 | 75.5 | 93.1 | 45.6 | 52.4 | 88.43 | -40.74% |  |  |  | 143707600
(b) Planned Outages | 80.5 | 75.2 | 63.6 | 53.8 | 39.1 | 25.9 | 27.6 | 15.3 | 12.1 | 12 | 40.51 | -70.38% |  |  |  | 134854800 |  |  |  | 135207350.79
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 143413200
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 77548800 |  |  |  | 0
Total of (a+b+c+d) | 185.2 | 176 | 183.6 | 167.1 | 133.1 | 110.8 | 103.1 | 108.4 | 57.7 | 64.4 | 128.94 | -50.05% | 185.2 | 57.7 | 93.1 | 86553600 | 70.7944 | 1 | 0 | 430353883.26
[10 empty] | 52.4 | [5 empty] | 70425600
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 68.81% | 70.85% | 66.71% | 63.85% | 66.26% | 64.45% | 60.32% | 59.04% | 67.3% | 66.61% | 65.42% | 1.819%
24 hours | 99.86% | 99.76% | 99.95% | 99.85% | 99.91% | 99.98% | 99.97% | 99.97% | 99.98% | 99.83% | 99.91% | -0.07607%
HV Faults:U/G no damage 3 hours | 84.4% | 95.04% | 89.74% | 97.79% | 89.51% | 93.94% | 93.94% | 92.47% | 95.66% | 95.74% | 92.82% | 3.143%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV Faults: U/G damage 3 hours | 90.37% | 89.33% | 91.89% | 90.98% | 92.56% | 93.27% | 93.27% | 94.13% | 95.64% | 95.38% | 92.68% | 2.911%
24 hours | 99.94% | 99.86% | 99.99% | 100% | 99.99% | 99.99% | 99.99% | 100% | 100% | 99.96% | 99.97% | -0.012%
HV Faults: O/H no damage 3 hours | 94.07% | 96.41% | 91.56% | 85.8% | 92.97% | 87.6% | 87.6% | 96.49% | 97.21% | 95.41% | 92.51% | 3.133%
24 hours | 99.99% | 99.98% | 100% | 100% | 100% | 99.98% | 99.98% | 100% | 100% | 100% | 99.99% | 0.007%
HV Faults: O/H damage 3 hours | 78.82% | 80.09% | 77.46% | 75.29% | 82.24% | 84.73% | 84.73% | 77.98% | 89.76% | 88.16% | 81.93% | 7.609%
24 hours | 99.96% | 100% | 99.95% | 100% | 99.99% | 100% | 100% | 99.02% | 100% | 100% | 99.89% | 0.1081%
HV Faults: Other 3 hours | [10 empty] | #DIV/0!
24 hours | [10 empty] | #DIV/0!
HV Faults: Total 3 hours | 88.41% | 87.29% | 87.53% | 84.49% | 89.98% | 89.61% | 91.74% | 87.29% | 93.99% | 93.2% | 89.35% | 4.305%
24 hours | 99.97% | 99.95% | 99.98% | 100% | 99.99% | 99.99% | 99.98% | 99.57% | 100% | 99.98% | 99.94% | 0.03902%
EHV Faults: 3 hours | 94.24% | 99.73% | 75.6% | 97.39% | 100% | 97.55% | 99.17% | 100% | 99.89% | 99.75% | 96.33% | 3.548%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.91% | 99.99% | -0.08101%
132kV F'lts: 3 hours | 100% | 100% | * | 100% | 78.5% | 100% | 100% | 100% | 100% | * | 77.85% | #VALUE!
24 hours | 100% | 100% | * | 100% | 100% | 100% | 100% | 100% | 100% | * | 80% | #VALUE!
Total Faults:3 hours | 87.74% | 87.9% | 83.81% | 85.16% | 88.11% | 90.01% | 91.45% | 88.03% | 93.44% | 93.7% | 88.94% | 5.358% | 93.7% | 83.81% |  | 1138432.512
24 hours | 99.96% | 99.94% | 99.98% | 99.99% | 99.99% | 99.99% | 99.98% | 99.67% | 100% | 99.96% | 99.95% | 0.01401% | 100% | 99.67% |  | 1214490.0096
TOTAL not rest in 3 hrs | 11.14% | 27.99% | 12.26% | 12.1% | 16.19% | 14.84% | 8.55% | 11.97% | 6.56% | 6.3% | 11.06% | -43.06% | 27.99% | 6.3% |  |  |  | 1 | 1
TOTAL not rest in 24 hrs | 0.15% | 6.94% | 0.04% | 0.06% | 0.02% | 0.01% | 0.02% | 0.33% | 0% | 0.04% | 0.054% | -25.93% | 6.94% | 0% |  |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
TOTAL |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
(b) due to plc action
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
Total |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 2.7 | 3.2 | 3.6 | 3.2 | 3.8 | 2 | 1.5 | 1 | 0.7 | 0.8 | 2.25 | 10 | 3.8 | 0.7 |  |  |  | 1 | 0
NOTES - * Information not available/applicable
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
| 20.7 | 19.2 | 17.6 | 19.7 | 17.5 | 18.6 | 18.8 | 15.9 | 15.9 | 15.6 | 17.95 | -4.361% | 20.7 | 15.6 |  |  |  | 1 | 1
5 RELEVANT DATA:
Number of Customers | 1245708 | 1255922 | 1267222 | 1277254 | 1289000 | 1297000 | 1308000 | 1323000 | 1344000 | 1344000
Embedded Gen.Stations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emb.Gen.Capacity MWSO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | %age overhead all voltages | 61.02%
Mains in commission (circuit kilometres)
Overhead Line
132kV |  |  | 1461 | 1461 | 1461 | 1461 | 1464 | 1464 | 1464 | 1464
66kV
33kV |  |  | 2785 | 2784 | 2795 | 2796 | 2800 | 2812 | 2817 | 2835
25kV
22kV
11kV |  |  | 17040 | 17060 | 17107 | 17189 | 17271 | 19031 | 17111 | 17120
6.6kV |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
3.3kV
3kV
2.2kV
LV |  |  | 7708 | 7699 | 7682 | 7664 | 7646 | 8911 | 7888 | 7834
TOTAL |  |  |  | 29018 | 29028 | 29069 | 29134 | 32242 | 29304 | 29277
Underground cable
132kV |  |  | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59
66kV
33kV |  |  | 969 | 971 | 977 | 978 | 981 | 982 | 929 | 929
25kV
22kV
11kV |  |  | 5939 | 6021 | 6114 | 6181 | 6248 | 6350 | 6408 | 6218
6.6kV |  |  | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 124
3.3kV
3kV
LV |  |  | 10799 | 10896 | 11006 | 11103 | 11200 | 11309 | 11185 | 11369
TOTAL |  |  |  |  | 17890 | 18071 | 18280 | 18445 | 18705 | 18699
47976
Transformers in commission
Primary voltage
| pole | ground mounted | agg. capacity (MVA)
132kV | 0 | 89 | 5565
66kV or 33kV | 0 | 540 | 7750
11kV and 6.6kV | 36782 | 11862 | 6751
TOTAL | 36782 | 12491 | 20066
49273
HV O/H length (km) | 16752.8889 | 16797.3333 | 16841.7778 | 16886.2222 | 16930.6667 | 16975.1111 | 17019.5556 | 17064 | 17135 | 17144
HV U/G length (km) | 5636 | 5697 | 5758 | 5819 | 5880 | 5941 | 6002 | 6063 | 6532 | 6342
SECURITY : customer supply interruptions per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 1.9892 | 2.8659 | 2.641 | 2.8535 | 1.3153 | 3.0564 | 2.8331 | 2.1821 | 2.2633 | 4.8742 | 2.6874 |  | 4.8742 | 1.3153
HV faults: U/G damage | 61.2245 | 56.2156 | 58.1012 | 48.7284 | 53.7083 | 49.9938 | 49.4695 | 39.4958 | 34.7728 | 32.8477 | 48.4557 |  | 61.2245 | 32.8477
HV faults: O/H no damage | 3.7922 | 5.0095 | 4.0631 | 7.7908 | 5.7862 | 5.4248 | 5.3797 | 5.7373 | 5.9611 | 7.2907 | 5.6236 |  | 7.7908 | 3.7922
HV faults: O/H damage | 17.3997 | 16.6735 | 14.2209 | 19.1366 | 15.2268 | 13.9823 | 13.9104 | 25.4304 | 12.0791 | 12.7 | 16.076 |  | 25.4304 | 12.0791
HV underground networks | 63.2137 | 59.0815 | 60.7421 | 51.5818 | 55.0236 | 53.0502 | 52.3026 | 41.6779 | 37.0361 | 37.7219 | 51.1431 |  | 63.2137 | 37.0361 |  |  |  | 1 | 0
HV overhead networks | 21.192 | 21.683 | 18.284 | 26.9274 | 21.013 | 19.4071 | 19.29 | 31.1677 | 18.0403 | 19.9907 | 21.6995 |  | 31.1677 | 18.0403 |  |  |  | 1 | 0
Availability : customer minutes lost per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 132.6162 | 176.3626 | 286.1043 | 263.3966 | 109.6088 | 218.3134 | 217.9274 | 152.7462 | 123.4538 | 296.6887 | 197.7218 |  | 296.6887 | 109.6088
HV faults: U/G damage | 5967.7282 | 6393.1434 | 6250.2787 | 4982.5856 | 4800.8673 | 3995.1355 | 3966.2779 | 2902.1771 | 2016.4115 | 2076.8212 | 4335.1427 |  | 6393.1434 | 2016.4115
HV faults: O/H no damage | 289.9954 | 366.3687 | 376.2138 | 915.2298 | 517.7115 | 511.9201 | 514.9136 | 325.6329 | 274.5258 | 368.4554 | 446.0967 |  | 915.2298 | 274.5258
HV faults: O/H damage | 2223.2983 | 2018.7665 | 1956.312 | 2874.2753 | 1865.2839 | 1512.8384 | 1506.3143 | 3799.0506 | 1003.9802 | 1097.5268 | 1985.7646 |  | 3799.0506 | 1003.9802
HV underground networks | 6100.3444 | 6569.506 | 6536.383 | 5245.9822 | 4910.4762 | 4213.4489 | 4184.2053 | 3054.9233 | 2139.8653 | 2373.5099 | 4532.8644 |  | 6569.506 | 2139.8653 |  |  |  | 1 | 0
HV overhead networks | 2513.2937 | 2385.1352 | 2332.5258 | 3789.5051 | 2382.9954 | 2024.7585 | 2021.2279 | 4124.6835 | 1278.506 | 1465.9823 | 2431.8613 |  | 4124.6835 | 1278.506 |  |  |  | 1 | 0
7484.256
7012.7479
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
| 1818733.68 | 1613859.77 | 1499123.626 | 1525041.276 | 1597071 | 1507114 | 1379940 | 1395765 | 1076544 | 1214976
| 230705121.6 | 221042272 | 232661959.2 | 213429143.4 | 171565900 | 143707600 | 134854800 | 143413200 | 77548800 | 86553600

## L
Yorkshire
Year: | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | * | 3.7628 | 3.82 | 3.37 | 3.73 | 2.41 | 2.36 | 2.52 | 2.3 | 1.69 | 2.5963
LV faults | 10.9842 | 7.0294 | 6.55 | 7.05 | 6.5 | 5.06 | 4.79 | 4.91 | 4.12 | 6.04 | 6.3034 | [8 empty] | 210382.9565
HV faults: U/G no damage | 2.85 | 2.14 | 1.9 | 0.74 | 2.19 | 2.79 | 2.27 | 3.8 | 2.34 | 5.79 | 2.681
HV faults: U/G damage | 21.93 | 21.9 | 23.08 | 25.17 | 28.69 | 26.83 | 27.83 | 23.15 | 24.01 | 23.81 | 24.64
HV faults: O/H no damage | 7.19 | 4.35 | 5.08 | 2.92 | 7.39 | 3.34 | 6.82 | 5.12 | 3.96 | 3.53 | 4.97
HV faults: O/H damage | 14.21 | 5.87 | 5.58 | 7.96 | 7.28 | 7.38 | 7.09 | 6.57 | 4.57 | 5.37 | 7.188 |  |  |  |  | 3137066
HV faults: All other | 9.9556 | 7.9511 | 10.01 | 11.62 | 13.14 | 14.58 | 15.52 | 14.73 | 20.38 | 14.29 | 13.2177 |  |  |  |  | 1374546
HV faults: Total | 56.1356 | 42.2111 | 45.65 | 48.41 | 58.69 | 54.92 | 59.53 | 53.37 | 55.26 | 52.78 | 52.6957 | 0.16% |  |  |  | 1439094.6864 |  |  |  | 1051399.902
EHV faults | 14.7568 | 6.2417 | 8.65 | 7.14 | 6.45 | 7.92 | 6.63 | 13.7 | 3.6 | 6.13 | 8.1218 | -24.52% |  |  |  | 1432705.4875 |  |  |  | 162049.528
132kV faults | 34.0074 | 2.4395 | 0.91 | 0 | 2.14 | 11.53 | 13.17 | 2 | 3.75 | 5.75 | 7.5697 | -24.04% |  |  |  | 1718358.3432 |  |  |  | 151032.852
Total of (a) | 115.884 | 61.6846 | 65.58 | 65.97 | 77.51 | 81.84 | 86.48 | 76.5 | 69.03 | 70.68 | 77.1159 | -8.346% |  |  |  | 1771544.3985
(b) Planned Outages | 7.3165 | 7.3753 | 6.29 | 5.08 | 5.05 | 4.65 | 4.44 | 3.5 | 2.76 | 2.35 | 4.8812 | -51.86% |  |  |  | 1918431.2352 |  |  |  | 97390.7095
(c) Embedded Gen. | * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1658397.6
(d) Other Systems | 35.2512 | 0 | 0 | 0 | 2.22 | 0 | 2.2 | 0 | 0 | 0 | 3.9671 |  |  |  |  | 1498918.4859 |  |  |  | 79153.1968
Total of (a+b+c+d) | 158.4518 | 69.0598 | 71.82 | 71.05 | 84.78 | 86.49 | 93.12 | 80 | 71.79 | 73.03 | 85.9592 | -15.04% | 158.4518 | 69.0598 |  | 1457116.469 | 81.3806 | 1 | 0 | 1715082.917
* inc service | [9 empty] | 70.68 | [5 empty] | 1410228.564
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | * | 3.7628 | 3.82 | 3.37 | [6 empty] | 2.7382
LV faults | 16.1817 | 13.0389 | 13.14 | 13.42 | 13.52 | 11.37 | 10.71 | 11.01 | 9.81 | 9.54 | 12.1741 | [8 empty] | 40632495.965
HV faults: U/G no damage | 1.69 | 1.07 | 1.05 | 0.37 | 1.62 | 1.62 | 1.36 | 2.47 | 1.65 | 3.75 | 1.665
HV faults: U/G damage | 15.76 | 14.49 | 15.69 | 17.74 | 19.59 | 18.66 | 18.33 | 15.32 | 17.35 | 16.31 | 16.924
HV faults: O/H no damage | 7.11 | 1.8 | 2.13 | 1.6 | 4.68 | 1.64 | 2.61 | 3.16 | 2.57 | 3.27 | 3.057
HV faults: O/H damage | 52.56 | 4.49 | 4.99 | 6.9 | 7.43 | 6.13 | 4.58 | 5.45 | 3.91 | 5.32 | 10.176 |  |  |  |  | 345739888.8
HV faults: All other | 7.09 | 4.26 | 4.67 | 6.88 | 7.58 | 7.84 | 7.62 | 8.82 | 10.95 | 8.11 | 7.382 |  |  |  |  | 118829340
HV faults: Total | 84.2036 | 26.1581 | 28.53 | 33.47 | 40.9 | 35.89 | 34.5 | 35.22 | 36.43 | 36.8 | 39.2102 | -6.147% |  |  |  | 118822493.6 |  |  |  | 130869011.888
EHV faults | 10.1689 | 0.88443 | 1.92 | 1.28 | 0.57 | 1.06 | 1.19 | 3.65 | 0.77 | 2.54 | 2.4033 | 5.687% |  |  |  | 122299208.75 |  |  |  | 8021436.4467
132kV faults | 33.5059 | 0.14638 | 0.01 | 0 | 0.38 | 2.5 | 1.89 | 0.77 | 0.78 | 0.06 | 4.0042 | -98.5% |  |  |  | 139021229.96 |  |  |  | 13364628.6463
Total of (a) | 144.0601 | 40.2278 | 43.57 | 48.17 | 55.38 | 50.83 | 48.29 | 50.65 | 47.79 | 48.93 | 57.7898 | -15.33% |  |  |  | 127586426.85
(b) Planned Outages | 18.6934 | 19.4743 | 15.73 | 12.48 | 12.84 | 11.46 | 10.88 | 8.45 | 5.91 | 4.73 | 12.0648 | -60.79% |  |  |  | 122992208.7 |  |  |  | 40267714.4388
(c) Embedded Gen. | * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 122514122.7
(d) Other Systems | 11.8781 | 0 | 0 | 0 | 0.38 | 0 | 0.53 | 0 | 0 | 0 | 1.2788 |  |  |  |  | 112121357.7 |  |  |  | 4268207.8304
Total of (a+b+c+d) | 174.6316 | 59.7021 | 59.3 | 60.65 | 68.59 | 62.29 | 59.7 | 59.1 | 53.7 | 53.66 | 71.1324 | -24.56% | 174.6316 | 53.66 |  | 107064041.8 | 70.7944 | 1 | 1 | 237413482.3282
[10 empty] | 48.93 | [5 empty] | 97626603.9
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 79.57% | 81.4% | 80.44% | 80.07% | 79.63% | 75.42% | 75.08% | 75.15% | 74.73% | 74.98% | 77.65% | -3.434%
24 hours | 99.14% | 99.92% | 99.86% | 99.94% | 100% | 100% | 100% | 100% | 100% | 100% | 99.89% | 0.1139%
HV Faults:U/G no damage 3 hours | 97.89% | 98.57% | 96.63% | 98.22% | 98.01% | 96.67% | 98.05% | 98.15% | 96.28% | 97.6% | 97.61% | -0.007172%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV Faults: U/G damage 3 hours | 96.36% | 97.59% | 95.9% | 96.23% | 96.94% | 96.65% | 96.94% | 96.64% | 96.17% | 97.17% | 96.66% | 0.5287%
24 hours | 99.95% | 99.94% | 99.97% | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 99.98% | 0.015%
HV Faults: O/H no damage 3 hours | 89.4% | 96.64% | 96.99% | 96.11% | 90.56% | 95.62% | 97.08% | 94.13% | 93.55% | 86.93% | 93.7% | -7.226%
24 hours | 99.07% | 100% | 100% | 100% | 99.99% | 100% | 100% | 100% | 100% | 100% | 99.91% | 0.09409%
HV Faults: O/H damage 3 hours | 59.01% | 92.49% | 90.25% | 88.77% | 85.09% | 90.76% | 94.78% | 91.49% | 90.29% | 86.43% | 86.94% | -0.582%
24 hours | 93.55% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.36% | 0.6492%
HV Faults: Other 3 hours | [10 empty] | #DIV/0!
24 hours | [10 empty] | #DIV/0!
HV Faults: Total 3 hours | 85.61% | 96.67% | 95.65% | 95.18% | 94.14% | 95.76% | 96.55% | 95.51% | 95.67% | 94.83% | 94.56% | 0.2887%
24 hours | 98.21% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.82% | 0.1793%
EHV Faults: 3 hours | 92.07% | 100% | 96.86% | 100% | 100% | 100% | 95.11% | 97.55% | 100% | 92.66% | 97.42% | -4.891%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.0002168%
132kV F'lts: 3 hours | 89.83% | 100% | 100% | 100% | 100% | 100% | 100% | 98.15% | 100% | 100% | 98.8% | 1.217%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
Total Faults:3 hours | 87.1% | 94.47% | 93.24% | 93.31% | 92.87% | 94.91% | 95.35% | 93.96% | 94.26% | 93.37% | 93.28% | 0.09219% | 95.35% | 87.1% |  | 1360509.6471
24 hours | 98.92% | 99.98% | 99.97% | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 99.89% | 0.1141% | 100% | 98.92% |  | 1457116.469
TOTAL not rest in 3 hrs | 6.718% | 8.401% | 12.9% | 5.533% | 6.76% | 6.69% | 7.13% | 6.04% | 5.74% | 6.63% | 7.254% | -8.604% | 12.9% | 5.533% |  |  |  | 1 | 0
TOTAL not rest in 24 hrs | 0.0873% | 0.06644% | 1.076% | 0.01678% | 0.03% | 0.01% | 0% | 0% | 0% | 0% | 0.1286% | -100% | 1.076% | 0% |  |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
(b) due to plc action
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 0.53 | 1.095 | 0.898 | 1.562 | 1.219 | 0.947 | 0.67 | 0.844 | 0.91 | 0.687 | 0.9362 | 10 | 1.562 | 0.53 |  |  |  | 1 | 0
* Overall reliability for 1991/2 affected by change in measured length of system
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
| 16.4347 | 14.788 | 14.9 | 15.48 | 17.04 | 15.07 | 14.93 | 14.27 | 12.71 | 12.17 | 14.7793 | 4.068% | 17.04 | 12.17 |  |  |  | 1 | 1
5 RELEVANT DATA:
Number of Customers | 1979824 | 1990370 | 2003752 | 2016475 | 2026844 | 2048265 | 2060171 | 2072997 | 2087921 | 1995230
Embedded Gen.Stations | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Emb.Gen.Capacity MWSO | 234 | 234 | 0 | 240 | 240 | 240 | 240 | 240 | 240 | 240
[9 empty] | %age overhead all voltages | 28.47%
Mains in commission (circuit kilometres)
Overhead Line
132kV |  |  |  | 0 | 1235 | 1235 | 1235 | 1235 | 1235 | 1222
66kV |  |  |  | 946 | 986 | 958 | 948 | 944 | 940 | 942
33kV |  |  |  | 1290 | 1325 | 1292 | 1316 | 1316 | 1291 | 1298
25kV |  |  |  | 0
22kV |  |  |  | 0
11kV |  |  |  | 9684 | 9724 | 9852 | 9836 | 9841 | 9851 | 9818
6.6kV |  |  |  | 0
3.3kV |  |  |  | 0
3kV |  |  |  | 0
2.2kV |  |  |  | 0
LV |  |  |  | 2678 | 2540 | 2574 | 2560 | 2554 | 2575 | 2537
TOTAL | [5 empty] | 15810 | 15911 | 15890 | 15892 | 15817
Underground cable
132kV |  |  |  | 174 | 174 | 174 | 179 | 179 | 174 | 179
66kV |  |  |  | 42 | 42 | 42 | 38 | 35 | 43 | 37
33kV |  |  |  | 1217 | 1218 | 1241 | 1180 | 1205 | 1241 | 1258
25kV |  |  |  | 0
22kV |  |  |  | 0
11kV |  |  |  | 10163 | 10181 | 10316 | 10202 | 10316 | 10444 | 10583
6.6kV |  |  |  | 18 | 18 | 18 | 18 | 18 | 18 | 8
3.3kV |  |  |  | 0
3kV |  |  |  | 0
LV |  |  |  | 26089 | 26112 | 26456 | 27132 | 27300 | 26456 | 27674
TOTAL | [6 empty] | 37745 | 38247 | 38376 | 39739
55556
Transformers in commission 1996/97
Primary voltage
Secondary >650 V | [7 empty] | 642 | 766 | 762
Secondary 650 V and under:
Pole Mounted | [7 empty] | 16616 | 16671 | 16665
Ground Mounted | [7 empty] | 14190 | 14338 | 14328
TOTAL | [7 empty] | 31448 | 31775 | 30993
Aggregate transforming Capacity (MVA)
Secondary >650 V | [7 empty] | 20777 | 20595 | 20668
Secondary 650 V and under: | [7 empty] | 9396 | 9455 | 9509
TOTAL | [7 empty] | 30173 | 30050 | 30177
HV O/H length (km) | 9396.2222 | 9395.3333 | 9394.4444 | 9393.5556 | 9392.6667 | 9391.7778 | 9390.8889 | 9390 | 9851 | 9818
HV U/G length (km) | 9741.5556 | 9797.3333 | 9853.1111 | 9908.8889 | 9964.6667 | 10020.4444 | 10076.2222 | 10132 | 10462 | 10591
SECURITY : customer supply interruptions per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 5.7922 | 4.3475 | 3.8639 | 1.5059 | 4.4545 | 5.703 | 4.6412 | 7.7748 | 4.67 | 10.9077 | 5.3661 |  | 10.9077 | 1.5059
HV faults: U/G damage | 44.5694 | 44.4908 | 46.936 | 51.2214 | 58.3563 | 54.8428 | 56.9008 | 47.3647 | 47.9172 | 44.8555 | 49.7455 |  | 58.3563 | 44.4908
HV faults: O/H no damage | 15.1496 | 9.2153 | 10.8352 | 6.2682 | 15.9469 | 7.2842 | 14.9617 | 11.3032 | 8.3932 | 7.1737 | 10.6531 |  | 15.9469 | 6.2682
HV faults: O/H damage | 29.9411 | 12.4354 | 11.9016 | 17.0874 | 15.7095 | 16.0951 | 15.554 | 14.5044 | 9.6861 | 10.913 | 15.3828 |  | 29.9411 | 9.6861
HV underground networks | 50.3616 | 48.8383 | 50.7999 | 52.7273 | 62.8109 | 60.5458 | 61.5421 | 55.1394 | 52.5872 | 55.7632 | 55.1116 |  | 62.8109 | 48.8383 |  |  |  | 0 | 0
HV overhead networks | 45.0907 | 21.6507 | 22.7368 | 23.3556 | 31.6564 | 23.3794 | 30.5157 | 25.8076 | 18.0793 | 18.0867 | 26.0359 |  | 45.0907 | 18.0793 |  |  |  | 1 | 0
Availability : customer minutes lost per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 343.467 | 217.3751 | 213.5305 | 75.2956 | 329.513 | 331.1419 | 278.0638 | 505.3595 | 329.2936 | 706.4595 | 332.9499 |  | 706.4595 | 75.2956
HV faults: U/G damage | 3202.9819 | 2943.7052 | 3190.7555 | 3610.1188 | 3984.6666 | 3814.2644 | 3747.7274 | 3134.4566 | 3462.5721 | 3072.6278 | 3416.3876 |  | 3984.6666 | 2943.7052
HV faults: O/H no damage | 1498.1073 | 381.324 | 454.3102 | 343.4653 | 1009.8974 | 357.6697 | 572.5812 | 697.622 | 544.7119 | 664.5347 | 652.4224 |  | 1498.1073 | 343.4653
HV faults: O/H damage | 11074.6156 | 951.1915 | 1064.3229 | 1481.1939 | 1603.3201 | 1336.8997 | 1004.7593 | 1203.1772 | 828.7251 | 1081.1391 | 2162.9344 |  | 11074.6156 | 828.7251
HV underground networks | 3546.4489 | 3161.0803 | 3404.286 | 3685.4144 | 4314.1796 | 4145.4064 | 4025.7912 | 3639.8161 | 3791.8657 | 3779.0873 | 3749.3376 |  | 4314.1796 | 3161.0803 |  |  |  | 0 | 0
HV overhead networks | 12572.7229 | 1332.5155 | 1518.6331 | 1824.6592 | 2613.2175 | 1694.5694 | 1577.3405 | 1900.7992 | 1373.437 | 1745.6738 | 2815.3568 |  | 12572.7229 | 1332.5155 |  |  |  | 1 | 0
customer minutes lost per circuit km
6761.1652
6312.8999
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
| 3137066 | 1374546 | 1439094.6864 | 1432705.4875 | 1718358.3432 | 1771544.3985 | 1918431.2352 | 1658397.6 | 1498918.4859 | 1457116.469
| 345739888.8 | 118829340 | 118822493.6 | 122299208.75 | 139021229.96 | 127586426.85 | 122992208.7 | 122514122.7 | 112121357.7 | 107064041.8

## M
Hydro-Electric
Year: | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 0.099 | 0.2768 | 0.255 | 0.23 | 0.9 | 1.2 | 0.5 | 1 | 1.4 | 1.5 | 0.73608
LV faults | 4.2 | 4.4 | 5.3 | 4.3 | 2 | 3 | 5 | 4 | 4 | 4 | 4.02 | [8 empty] | 134172.6858
HV faults: U/G no damage | 0.17 | 0.9 | 0.68 | 0.39 | 0.6 | 0.5 | 0.5 | 0.5 | 0.8 | 0 | 0.504
HV faults: U/G damage | 14.64 | 13.93 | 17.18 | 16.24 | 17 | 16 | 13 | 15.5 | 16.4 | 19.7 | 15.959
HV faults: O/H no damage | 13.27 | 15.66 | 20.32 | 19.25 | 20 | 17 | 16 | 15.4 | 15.2 | 14.3 | 16.64
HV faults: O/H damage | 25.71 | 34.32 | 49.94 | 38.74 | 29 | 39 | 26 | 29.3 | 30.2 | 28.6 | 33.081 |  |  |  |  | 1040282.1
HV faults: All other | 36.63 | 40.75 | 46.98 | 32.58 | 27.4 | 36.5 | 24.5 | 25.4 | 25.4 | 23.1 | 31.924 |  |  |  |  | 1214632.3323
HV faults: Total | 90.42 | 105.56 | 135.1 | 107.2 | 94 | 109 | 80 | 86.1 | 88 | 85.7 | 98.108 | -12.65% |  |  |  | 1395920.8644 |  |  |  | 627891.2
EHV faults | 35 | 48.4 | 55.4 | 34.2 | 46 | 53 | 33 | 38 | 39 | 37 | 41.9 | -11.69% |  |  |  | 1066320 |  |  |  | 268160
132kV faults | [11 empty] | #DIV/0! |  |  |  | 1126400 |  |  |  | 0
Total of (a) | 129.719 | 158.6368 | 196.055 | 145.73 | 144 | 167 | 118 | 129.1 | 133 | 128 | 144.9241 | -11.68% |  |  |  | 1215900
(b) Planned Outages | 28.6 | 26.7 | 24.4 | 26.8 | 27 | 27 | 29 | 24 | 22 | 13 | 24.85 | -47.69% |  |  |  | 934400 |  |  |  | 159040
(c) Embedded Gen. | 18 | 18.8 | 14.15 | 5.19 | 5 | 0 | 0 | 0 | 0 | 0 | 6.114 |  |  |  |  | 979840
(d) Other Systems | * | * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 992000 |  |  |  | 39129.6
Total of (a+b+c+d) | 176.319 | 204.1368 | 234.605 | 177.72 | 176 | 193 | 146 | 153.1 | 155 | 141 | 175.6881 | -19.74% | 234.605 | 141 |  | 902400 | 81.3806 | 1 | 1 | 1124403.712
[10 empty] | 128 | [5 empty] | 819200
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults |  |  | 1.89 | 1.65 | 1 | 1 | 1 | 1.3 | 2 | 1.7 | 1.4425
LV faults | 7.4 | 7.6 | 10 | 7.9 | 5 | 8 | 8 | 7 | 8 | 5 | 7.39 | [8 empty] | 24665078.31
HV faults: U/G no damage | 0.46 | 0.63 | 0.34 | 0.23 | 0.6 | 0.3 | 0.5 | 0.6 | 0.6 | 0 | 0.426
HV faults: U/G damage | 14.55 | 15.26 | 18.52 | 18.68 | 21 | 22 | 17.1 | 16.8 | 20.2 | 12.3 | 17.641
HV faults: O/H no damage | 8.2 | 16.87 | 18.46 | 17.53 | 16 | 18 | 11.3 | 11.7 | 14.5 | 12.5 | 14.506
HV faults: O/H damage | 35.95 | 75.69 | 124.6 | 71.9 | 49 | 142 | 40.9 | 63 | 52.5 | 32.1 | 68.764 |  |  |  |  | 101491800
HV faults: All other | 22.36 | 31.76 | 49.58 | 25.76 | 25.4 | 34.7 | 18.9 | 22.1 | 24.2 | 15.1 | 26.986 |  |  |  |  | 160807132.34
HV faults: Total | 81.52 | 140.21 | 211.5 | 134.1 | 112 | 217 | 88.7 | 114.2 | 112 | 72 | 128.323 | -43.89% |  |  |  | 211716102.38 |  |  |  | 428294566.167
EHV faults | 16.1 | 49.4 | 60 | 36.6 | 42 | 66 | 26 | 30 | 43 | 21 | 39.01 | -46.17% |  |  |  | 152472000 |  |  |  | 130200907.29
132kV faults | [11 empty] | #DIV/0! |  |  |  | 149120000 |  |  |  | 0
Total of (a) | 105.02 | 197.21 | 283.39 | 180.25 | 160 | 293 | 124 | 152.5 | 165 | 99 | 175.937 | -43.73% |  |  |  | 229950000
(b) Planned Outages | 64 | 70 | 68.4 | 73.2 | 72 | 72 | 82 | 67 | 55 | 24 | 64.76 | -62.94% |  |  |  | 131840000 |  |  |  | 216144854.04
(c) Embedded Gen. | 3 | 3.05 | 4.03 | 0.67 | 1 | 0 | 0 | 0 | 0 | 0 | 1.175 |  |  |  |  | 140480000
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 140800000 |  |  |  | 3921714.075
Total of (a+b+c+d) | 172.02 | 270.26 | 355.82 | 254.12 | 233 | 365 | 206 | 219.5 | 220 | 123 | 241.872 | -49.15% | 365 | 123 |  | 78720000 | 70.7944 | 1 | 1 | 807279001.488
[10 empty] | 99 | [5 empty] | 63360000
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 76% | 77.34% | 71.68% | 70.3% | 72% | 66% | 74.05% | 74.72% | 74% | 81% | 73.71% | 9.892%
24 hours | 99% | 99.25% | 98.27% | 99.73% | 100% | 99% | 99.93% | 99.48% | 99.71% | 100% | 99.44% | 0.5662%
HV Faults:U/G no damage 3 hours | 59.7% | 90.96% | 97.47% | 100% | 92.45% | 85.34% | 86.57% | 91.7% | 100% | 100% | 90.42% | 10.6%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV Faults: U/G damage 3 hours | 92.73% | 90% | 91.11% | 89.25% | 84.72% | 84.37% | 84.84% | 90.4% | 61.1% | 95.6% | 86.41% | 10.63%
24 hours | 99.93% | 99.62% | 99.94% | 100% | 99.99% | 99.81% | 99.99% | 100% | 99.9% | 100% | 99.92% | 0.08207%
HV Faults: O/H no damage 3 hours | 94.09% | 86.39% | 90.31% | 88.04% | 89.88% | 84.36% | 91.44% | 91.2% | 95.1% | 82.2% | 89.3% | -7.952%
24 hours | 100% | 99.98% | 99.87% | 100% | 100% | 99.74% | 100% | 100% | 99.7% | 100% | 99.93% | 0.07105%
HV Faults: O/H damage 3 hours | 78.23% | 69.94% | 60.8% | 69.68% | 67.07% | 53.99% | 70.7% | 67.5% | 86.8% | 81.9% | 70.66% | 15.91%
24 hours | 99.91% | 98.15% | 98.22% | 99.17% | 99.88% | 93.68% | 99.92% | 99.6% | 99% | 99.6% | 98.71% | 0.8986%
HV Faults: Other 3 hours |  |  |  | 90.62% | [6 empty] | 90.62%
24 hours |  |  |  | 99.14% | [6 empty] | 99.14%
HV Faults: Total 3 hours | 88.7% | 83.25% | 78.17% | 82.83% | 80.46% | 73.58% | 83.13% | 82.45% | 82% | 89.8% | 82.44% | 8.932%
24 hours | 99.95% | 99.19% | 99.22% | 99.66% | 99.94% | 97.63% | 99.66% | 99.83% | 97.18% | 99.9% | 99.22% | 0.6894%
EHV Faults: 3 hours | 96% | 84.93% | 87.63% | 82.5% | 87% | 84% | 87.8% | 90.55% | 86% | 95% | 88.14% | 7.782%
24 hours | 99% | 99.58% | 99.59% | 99.98% | 100% | 100% | 99.97% | 99.83% | 96.71% | 100% | 99.47% | 0.5369%
132kV F'lts: 3 hours | [10 empty] | #DIV/0! | #DIV/0!
24 hours | [10 empty] | #DIV/0! | #DIV/0!
Total Faults:3 hours | 88.7% | 83.25% | 78.17% | 82.83% | 80.46% | 73.58% | 83.15% | 84.58% | 83% | 91% | 82.87% | 9.808% | 91% | 73.58% |  | 821184
24 hours | 99.95% | 99.19% | 99.22% | 99.66% | 99.94% | 97.63% | 99.66% | 99.82% | 97.15% | 100% | 99.22% | 0.7841% | 100% | 97.15% |  | 902400
TOTAL not rest in 3 hrs | 11.3% | 16.75% | 21.83% | 17.17% | 19.54% | 26.42% | 16.85% | 15.42% | 17% | 9% | 17.13% | -47.45% | 26.42% | 9% |  |  |  | 1 | 1
TOTAL not rest in 24 hrs | 0.05% | 0.81% | 0.78% | 0.34% | 0.06% | 2.37% | 0.34% | 0.18% | 2.85% | 0% | 0.778% | -100% | 2.85% | 0% |  |  |  | 1 | 1
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | * | *
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | * | *
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | * | *
(b) due to plc action
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | * | *
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | * | *
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | * | *
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 2.2203 | 1.9832 | 3.479 | 5.9 | 6.1 | 4 | 4 | 4.41 | 2.6 | 1.5 | 3.6193 | 10 | 6.1 | 1.5 |  |  |  | 1 | 1
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
| 13.9 | 12.4 | 15.49 | 12.49 | 11 | 13 | 15.14 | 15.86 | 16.07 | 15.5 | 14.085 | -2.28% | 16.07 | 11 |  |  |  | 0 | 0
5 RELEVANT DATA:
Total Connected Customers (millions) | 590000 | 595009 | 595009 | 600000 | 640000 | 630000 | 640000 | 640000 | 640000 | 640000
Embedded Gen.Stations | 153 | 153 | 152 | 159 | 172 | 164 | 164 | 164 | 164 | 167
Emb.Gen.Capacity MWSO | 401 | 391 | 369 | 420 | 422 | 365 | 365 | 365 | 365 | 406
[9 empty] | %age overhead all voltages | 68.28%
Mains in commission (circuit kilometres)
Overhead Line
33kV |  |  | 5242 | 5242 | 5119 | 4949 | 5131 | 5315 | 5422 | 5325
22kV |  |  | 248 | 248 | 143 | 151.6 | 152 | 0 | 0 | 0
11kV |  |  | 20635 | 20635 | 23371 | 22264 | 21314 | 20793 | 20905 | 20823
6.6kV |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LV |  |  | 6683 | 6683 | 5648 | 5339 | 4363 | 4299 | 4035 | 4299
TOTAL |  |  | 32808 | 32808 | 34281 | 32703.6 | 30960 | 30407 | 30362 | 30447
L.V. Services | [6 empty] | 2030
Underground cable
33kV |  |  | 469 | 469 | 592 | 592 | 601 | 640 | 566 | 640
22kV |  |  | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0
11kV |  |  | 3979 | 3979 | 4433 | 4440 | 4570 | 4606 | 4435 | 4702
6.6kV |  |  | 146 | 146 | 9.4 | 9.4 | 9 | 0 | 0 | 0
LV |  |  | 7329 | 7329 | 8057 | 8111 | 8514 | 8709 | 8750 | 8800
TOTAL |  |  | 11923 | 11923 | 13106.4 | 13167.4 | 13709 | 13955 | 13751 | 14142
44589
Transformers
Transformers in commission
TYPES OF TRANSFORMER | AGGREGATE TRANSFORMING
CAPACITY (MVA)
| pole mounted | ground mounted | aggregate capacity (MVA)
33 kV / 11 or 6.6 kV | 40 | 515 | 5050
22 kV / 11 or 6.6 kV | 0 | 0 | 0
33 kV / LV | 1535 | 6 | 65
22 kV / LV | 0 | 0 | 0
11 kV / LV | 39562 | 6276 | 4950
6.6 kV / LV | 0 | 0 | 0
Total | 41137 | 6797 | 10065
47934
HV O/H length (km) | 19852.4591 | 19964.2506 | 20635 | 20635 | 23371 | 22264 | 21314 | 20793 | 20905 | 20823
HV U/G length (km) | 3968.5677 | 3990.9151 | 4125 | 4125 | 4442.4 | 4449.4 | 4579 | 4606 | 4435 | 4702
SECURITY : customer supply interruptions per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 0.25274 | 1.3418 | 0.98086 | 0.56727 | 0.8644 | 0.70796 | 0.69884 | 0.69475 | 1.1545 | 0 | 0.72631 |  | 1.3418 | 0
HV faults: U/G damage | 21.765 | 20.7684 | 24.7812 | 23.6218 | 24.4913 | 22.6547 | 18.1699 | 21.5371 | 23.6663 | 26.8141 | 22.827 |  | 26.8141 | 18.1699
HV faults: O/H no damage | 3.9437 | 4.6673 | 5.8593 | 5.5973 | 5.4769 | 4.8105 | 4.8044 | 4.7401 | 4.6534 | 4.3951 | 4.8948 |  | 5.8593 | 3.9437
HV faults: O/H damage | 7.6408 | 10.2286 | 14.4002 | 11.2644 | 7.9415 | 11.0358 | 7.8071 | 9.0184 | 9.2456 | 8.7903 | 9.7373 |  | 14.4002 | 7.6408
HV underground networks | 22.0178 | 22.1102 | 25.7621 | 24.1891 | 25.3557 | 23.3627 | 18.8687 | 22.2319 | 24.8207 | 26.8141 | 23.5533 |  | 26.8141 | 18.8687 |  |  |  | 0 | 0
HV overhead networks | 11.5846 | 14.8959 | 20.2594 | 16.8616 | 13.4183 | 15.8462 | 12.6114 | 13.7585 | 13.8991 | 13.1854 | 14.632 |  | 20.2594 | 11.5846 |  |  |  | 1 | 0
Availability : customer minutes lost per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 68.3874 | 93.9272 | 49.0432 | 33.4545 | 86.4398 | 42.4776 | 69.8843 | 83.3695 | 86.584 | 0 | 61.3568 |  | 93.9272 | 0
HV faults: U/G damage | 2163.123 | 2275.1266 | 2671.4101 | 2717.0909 | 3025.3917 | 3115.0267 | 2390.0415 | 2334.3465 | 2914.9944 | 1674.1812 | 2528.0733 |  | 3115.0267 | 1674.1812
HV faults: O/H no damage | 243.6978 | 502.7888 | 532.293 | 509.7165 | 438.1498 | 509.3424 | 339.3075 | 360.1212 | 443.9129 | 384.1906 | 426.3521 |  | 532.293 | 243.6978
HV faults: O/H damage | 1068.4067 | 2255.8438 | 3592.8336 | 2090.6227 | 1341.8339 | 4018.1459 | 1228.113 | 1939.1141 | 1607.271 | 986.6014 | 2012.8786 |  | 4018.1459 | 986.6014
HV underground networks | 2231.5104 | 2369.0539 | 2720.4533 | 2750.5455 | 3111.8314 | 3157.5044 | 2459.9257 | 2417.716 | 3001.5784 | 1674.1812 | 2589.43 |  | 3157.5044 | 1674.1812 |  |  |  | 1 | 1
HV overhead networks | 1312.1045 | 2758.6326 | 4125.1266 | 2600.3392 | 1779.9837 | 4527.4883 | 1567.4205 | 2299.2353 | 2051.1839 | 1370.7919 | 2439.2307 |  | 4527.4883 | 1312.1045 |  |  |  | 1 | 0
6911.295
6289.2784
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
| 1040282.1 | 1214632.3323 | 1395920.8644 | 1066320 | 1126400 | 1215900 | 934400 | 979840 | 992000 | 902400
| 101491800 | 160807132.34 | 211716102.38 | 152472000 | 149120000 | 229950000 | 131840000 | 140480000 | 140800000 | 78720000

## N
ScottishPower
Year: | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | * | 1.8 | 1.7 | 1.49 | 1.67 | 1.38 | 1.34 | 2.17 | 2.12 | 2.14 | 1.581
LV faults | 7.03 | 7.44 | 7.1 | 6.97 | 5.84 | 5.69 | 5.38 | 7.86 | 6.81 | 6.28 | 6.64 | [8 empty] | 221618.5656
HV faults: U/G no damage | 1.3 | 2.65 | 1.42 | 1.15 | 2.48 | 0.33 | 0.25 | 0.87 | 0.55 | 1.04 | 1.204
HV faults: U/G damage | 15.94 | 17.22 | 14.73 | 14.8 | 14.35 | 16.11 | 17 | 21.78 | 22.37 | 21.87 | 17.617
HV faults: O/H no damage | 5.69 | 4.57 | 8.64 | 5.69 | 4.19 | 5.49 | 4.83 | 7.64 | 8.5 | 5.89 | 6.113
HV faults: O/H damage | 7.68 | 5.87 | 10.31 | 8.14 | 6.39 | 8.1 | 7.84 | 8.1 | 15.26 | 9.66 | 8.735 |  |  |  |  | 1210581.0106
HV faults: All other | 11.92 | 9.31 | 10.67 | 8.34 | 7.61 | 12.45 | 10.36 | 11.98 | 13.27 | 13.89 | 10.98 |  |  |  |  | 1228116.6881
HV faults: Total | 42.53 | 39.56 | 45.8 | 38.12 | 35.02 | 42.48 | 40.28 | 50.37 | 59.95 | 52.35 | 44.646 | 17.26% |  |  |  | 1454977.956 |  |  |  | 839344.8
EHV faults | 11.44 | 14.3 | 10.6 | 6.23 | 9.51 | 8.79 | 5.88 | 10.2 | 9.08 | 9.46 | 9.549 | -0.932% |  |  |  | 1023636.374 |  |  |  | 179521.2
132kV faults | [11 empty] | #DIV/0! |  |  |  | 1081116 |  |  |  | 0
Total of (a) | 61 | 61.3 | 63.5 | 51.32 | 50.37 | 56.96 | 51.54 | 68.43 | 75.84 | 68.09 | 60.835 | 11.93% |  |  |  | 1178280
(b) Planned Outages | 6.73 | 6.32 | 5.6 | 4.77 | 4.48 | 3.76 | 2.36 | 2.04 | 1.8 | 1.88 | 3.974 | -52.69% |  |  |  | 1026180 |  |  |  | 74711.2
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.04 | 0 | 0 | 0.104 |  |  |  |  | 1356870
(d) Other Systems | 2.74 | 3.35 | 14 | 2.09 | 6.23 | 4.74 | 3.11 | 1.44 | 8.11 | 12.27 | 5.808 |  |  |  |  | 1603525 |  |  |  | 111145.6
Total of (a+b+c+d) | 70.46 | 70.97 | 83.1 | 58.18 | 61.08 | 65.46 | 57.01 | 72.95 | 85.75 | 82.24 | 70.72 | 16.29% | 85.75 | 57.01 | 51.03 | 1546112 | 81.3806 | 0 | 0 | 1329536
[10 empty] | 80.36 | [5 empty] | 1510768
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults |  |  |  |  | 1.89 |  |  |  |  | 2.9 | 2.395
LV faults | 11.83 | 11.77 | 11.8 | 11.33 | 9.37 | 9.5 | 9.66 | 9.69 | 11.35 | 8.61 | 10.491 | [8 empty] | 35015065.839
HV faults: U/G no damage | 1.3 | 2.31 | 1.45 | 1.34 | 2.31 | 0.39 | 0.37 | 0.87 | 0.61 | 0.67 | 1.162
HV faults: U/G damage | 15.92 | 16.81 | 15.3 | 15.92 | 15.96 | 17.92 | 21.06 | 23.17 | 23.74 | 23.24 | 18.904
HV faults: O/H no damage | 6.14 | 4.12 | 11.78 | 5.49 | 4.14 | 6.67 | 6.22 | 6.74 | 21.81 | 5.71 | 7.882
HV faults: O/H damage | 12.26 | 8.25 | 22.36 | 13.53 | 8.65 | 13.07 | 26.21 | 11.44 | 74.88 | 12.95 | 20.36 |  |  |  |  | 146554868.3
HV faults: All other | 10.93 | 7.56 | 10.71 | 6.97 | 6.88 | 13.88 | 10.45 | 11.1 | 16.79 | 11.62 | 10.689 |  |  |  |  | 130789149.34
HV faults: Total | 46.55 | 39.05 | 61.6 | 43.25 | 37.94 | 51.93 | 64.31 | 53.32 | 137.83 | 54.19 | 58.997 | -8.148% |  |  |  | 170710410 |  |  |  | 196910098.113
EHV faults | 8.47 | 7.06 | 7.6 | 4.46 | 8.72 | 8.5 | 7.81 | 6.77 | 16.34 | 6.67 | 8.24 | -19.05% |  |  |  | 135388138.5 |  |  |  | 27502062.96
132kV faults | [11 empty] | #DIV/0! |  |  |  | 123758400 |  |  |  | 0
Total of (a) | 66.85 | 57.88 | 81 | 59.04 | 56.03 | 69.93 | 81.78 | 69.78 | 165.52 | 69.47 | 77.728 | -10.62% |  |  |  | 145854000
(b) Planned Outages | 18.35 | 16.76 | 14 | 12.82 | 11.63 | 9.9 | 6.07 | 4.94 | 4.69 | 4.22 | 10.338 | -59.18% |  |  |  | 159426000 |  |  |  | 34504408.602
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0.24 |  |  |  |  | 143889600
(d) Other Systems | 0.1 | 0.94 | 2.5 | 5.09 | 2.26 | 1.2 | 0.72 | 0.24 | 7.1 | 2.89 | 2.304 |  |  |  |  | 331569700 |  |  |  | 8490928.176
Total of (a+b+c+d) | 85.3 | 75.58 | 97.5 | 76.95 | 69.92 | 81.03 | 88.57 | 77.36 | 177.31 | 76.58 | 90.61 | -15.48% | 177.31 | 69.92 | 61.9 | 143970400 | 70.7944 | 1 | 0 | 302422563.69
[10 empty] | 72.36 | [5 empty] | 136036800
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 71.81% | 72.22% | 71.8% | 71.84% | 73.28% | 70.6% | 67.5% | 80.5% | 82.1% | 79.1% | 74.08% | 6.784%
24 hours | 99.69% | 99.6% | 99.4% | 99.79% | 99.84% | 99.6% | 99.2% | 99.9% | 98.4% | 100% | 99.54% | 0.4601%
HV Faults:U/G no damage 3 hours | 86% | 93.7% | 90.6% | 80.98% | 89.23% | 77.9% | 53% | 89.3% | 80.2% | 93% | 83.39% | 11.52%
24 hours | 100% | 100% | 100% | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.001%
HV Faults: U/G damage 3 hours | 91.6% | 92.5% | 91.3% | 90.68% | 88.17% | 87.9% | 85.8% | 88.9% | 89.5% | 89.7% | 89.61% | 0.106%
24 hours | 100% | 100% | 100% | 99.98% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.002%
HV Faults: O/H no damage 3 hours | 89.4% | 91.7% | 80.2% | 91.89% | 88.51% | 85.2% | 84.7% | 90% | 71% | 88.4% | 86.1% | 2.671%
24 hours | 99.9% | 100% | 100% | 100% | 100% | 99.4% | 99.8% | 100% | 97.6% | 100% | 99.67% | 0.3311%
HV Faults: O/H damage 3 hours | 74.3% | 76.3% | 61.9% | 70.45% | 77.06% | 73.1% | 64.5% | 76.2% | 59.7% | 72.5% | 70.6% | 2.69%
24 hours | 99.5% | 100% | 99.9% | 99.99% | 100% | 99.3% | 95% | 100% | 91.2% | 100% | 98.49% | 1.534%
HV Faults: Other 3 hours | [10 empty] | #DIV/0!
24 hours | [10 empty] | #DIV/0!
HV Faults: Total 3 hours | 87.16% | 90.22% | 81.8% | 86.37% | 87.06% | 84.3% | 82.3% | 87.3% | 78.7% | 86% | 85.12% | 1.033%
24 hours | 99.84% | 99.98% | 100% | 99.99% | 99.93% | 99.8% | 99% | 100% | 97.2% | 100% | 99.57% | 0.4278%
EHV Faults: 3 hours | 94.99% | 97.01% | 91% | 95.14% | 90.3% | 92% | 81.5% | 97.6% | 74.3% | 96.4% | 91.02% | 5.906%
24 hours | 99.68% | 99.88% | 99.8% | 99.99% | 99.91% | 99.4% | 99.9% | 100% | 96.3% | 100% | 99.49% | 0.5167%
132kV F'lts: 3 hours | [10 empty] | #DIV/0! | #DIV/0!
24 hours | [10 empty] | #DIV/0! | #DIV/0!
Total Faults:3 hours | 86.86% | 89.66% | 82.3% | 85.46% | 86.15% | 85.6% | 80.6% | 88% | 78.4% | 86.8% | 84.98% | 2.138% | 89.66% | 78.4% |  | 1342025.216
24 hours | 99.79% | 99.91% | 99.8% | 99.96% | 99.97% | 99.7% | 99.1% | 100% | 97.2% | 100% | 99.54% | 0.4591% | 100% | 97.2% |  | 1546112
TOTAL not rest in 3 hrs | 12.85% | 11.93% | 13.14% | 10.34% | 16.8% | 14.4% | 16.1% | 12% | 21.6% | 13.2% | 15.02% | -12.1% | 21.6% | 10.34% | 16.2% |  |  | 1 | 0
TOTAL not rest in 24 hrs | 0.2% | 0.18% | 0.21% | 0.09% | 0.2% | 0.3% | 0.9% | 0% | 2.8% | 0% | 0.457% | -100% | 2.8% | 0% | 0.1% |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
At GCC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N / A | N / A
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N / A | N / A
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N / A | N / A
(b) due to plc action
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N / A | N / A
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N / A | N / A
Totals | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N / A | N / A
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
|  | 2.26 | 2.3 | 3.24 | 2.38 | 1.91 | 2.89 | 2.42 | 2.2 | 1.45 | 2.3389 | 9 | 3.24 | 1.45 |  |  |  | 1 | 1
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
| 16.91 | 17.16 | 19.4 | 17.81 | 15.33 | 17.5 | 15.7 | 14.93 | 17.06 | 14.38 | 16.618 |  | 19.4 | 14.38 | 14.71 |  |  | 1 | 1
RELEVANT DATA:
Number of Customers | 1718111 | 1730473 | 1750876 | 1759430 | 1770000 | 1800000 | 1800000 | 1860000 | 1870000 | 1880000
Embedded Gen.Stations | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Emb.Gen.Capacity MWSO | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59
[9 empty] | %age overhead all voltages | 37.74%
Mains in commission (circuit kilometres)
Overhead Line
EHV |  |  | 2905 | 2901 | 3000 | 3000 | 3015 | 3018 | 3012 | 3012
HV |  |  | 14975 | 15149 | 15774 | 15827 | 16618 | 16654 | 16773 | 16864
3.3kV
3kV
L.V. Main |  |  | 4525 | 4439 | 4646 | 4640 | 4633 | 4628 | 4607 | 4572
TOTAL |  |  |  | 22405 | 22489 | 25144 | 25191 | 24300 | 24392 | 24448
L.V. Services |  |  |  |  | 2030 | 2030
Underground cable
EHV |  |  | 1623 | 1637 | 1658 | 1662 | 1672 | 1697 | 1727 | 1737
HV |  |  | 13888 | 14001 | 14250 | 14403 | 14532 | 14674 | 14794 | 14910
3.3kV
3kV
L.V. Main |  |  | 21663 | 21998 | 22392 | 22637 | 22927 | 23273 | 23483 | 23690
TOTAL |  |  |  |  | 37174 | 38702 | 38458 | 38860 | 40004 | 40337
[8 empty] | 22042 | 22584 | 64785
TYPES OF TRANSFORMER | POLE MOUNTED |  | GROUND MOUNTED |  | AGGREGATE TRANSFORMING
CAPACITY (MVA)
33 kV / 11 or 6.6 kV | 0 |  | 754 |  | 12996
11 or 6.6 kV / LV | 23587 |  | 15642 |  | 10359
Total | 23587 |  | 16396 |  | 23355
39983
HV O/H length (km) | 14810.1111 | 14833.6667 | 14857.2222 | 14880.7778 | 14904.3333 | 14927.8889 | 14951.4444 | 14975 | 16773 | 16864
HV U/G length (km) | 12950 | 13084 | 13218 | 13352 | 13486 | 13620 | 13754 | 13888 | 14794 | 14910
SECURITY : customer supply interruptions per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 1.7247 | 3.5049 | 1.881 | 1.5154 | 3.2549 | 0.43612 | 0.32718 | 1.1652 | 0.69521 | 1.3113 | 1.5816 |  | 3.5049 | 0.32718
HV faults: U/G damage | 21.148 | 22.775 | 19.5116 | 19.5024 | 18.834 | 21.2907 | 22.2481 | 29.1696 | 28.2763 | 27.5759 | 23.0331 |  | 29.1696 | 18.834
HV faults: O/H no damage | 6.6009 | 5.3313 | 10.182 | 6.7276 | 4.9759 | 6.6198 | 5.8148 | 9.4894 | 9.4765 | 6.5662 | 7.1784 |  | 10.182 | 4.9759
HV faults: O/H damage | 8.9095 | 6.8479 | 12.15 | 9.6243 | 7.5886 | 9.767 | 9.4386 | 10.0608 | 17.0132 | 10.769 | 10.2169 |  | 17.0132 | 6.8479
HV underground networks | 22.8728 | 26.2798 | 21.3925 | 21.0178 | 22.0889 | 21.7269 | 22.5753 | 30.3348 | 28.9715 | 28.8872 | 24.6147 |  | 30.3348 | 21.0178 |  |  |  | 0 | 0
HV overhead networks | 15.5104 | 12.1791 | 22.332 | 16.3519 | 12.5645 | 16.3868 | 15.2534 | 19.5502 | 26.4897 | 17.3352 | 17.3953 |  | 26.4897 | 12.1791 |  |  |  | 1 | 0
Availability : customer minutes lost per circuit km | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 10 Yr Avg
HV faults: U/G no damage | 172.4745 | 305.5176 | 192.0692 | 176.5755 | 303.1811 | 51.5419 | 48.4223 | 116.5179 | 77.1056 | 84.4802 | 152.7886 |  | 305.5176 | 48.4223
HV faults: U/G damage | 2112.1488 | 2223.269 | 2026.6608 | 2097.8225 | 2094.7056 | 2368.2819 | 2756.1437 | 3103.125 | 3000.7976 | 2930.3286 | 2471.3284 |  | 3103.125 | 2026.6608
HV faults: O/H no damage | 712.2973 | 480.6329 | 1388.2352 | 649.1106 | 491.6557 | 804.2664 | 748.824 | 837.1553 | 2431.5686 | 636.5512 | 918.0297 |  | 2431.5686 | 480.6329
HV faults: O/H damage | 1422.2743 | 962.4325 | 2635.0543 | 1599.7207 | 1027.2516 | 1575.9764 | 3155.4142 | 1420.9282 | 8348.274 | 1443.667 | 2359.0993 |  | 8348.274 | 962.4325
HV underground networks | 2284.6233 | 2528.7866 | 2218.73 | 2274.398 | 2397.8867 | 2419.8238 | 2804.5659 | 3219.6429 | 3077.9032 | 3014.8089 | 2624.1169 |  | 3219.6429 | 2218.73 |  |  |  | 0 | 0
HV overhead networks | 2134.5716 | 1443.0654 | 4023.2895 | 2248.8313 | 1518.9073 | 2380.2428 | 3904.2382 | 2258.0835 | 10779.8426 | 2080.2182 | 3277.129 |  | 10779.8426 | 1443.0654 |  |  |  | 1 | 0
9316.083
8086.36
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
| 1210581.0106 | 1228116.6881 | 1454977.956 | 1023636.374 | 1081116 | 1178280 | 1026180 | 1356870 | 1603525 | 1546112
| 146554868.3 | 130789149.34 | 170710410 | 135388138.5 | 123758400 | 145854000 | 159426000 | 143889600 | 331569700 | 143970400

## O
USED IN GRAPHS ON THIS SHEET
Vertical line indicates range over 10 years
Vertical line indicates range since recording started
SECURITY - Supply Interruptions per 100 connected Customers
NUMBER OF INTERRUPTIONS/100 CUSTOMERS
AVAILABILITY - Minutes Lost per connected Customer
NUMBER OF MINUTES LOST/CUSTOMER
RESTORATION OF SUPPLY - Percentage of Interruptions Not Restored within 3 hours
PERCENTAGE NOT RESTORED
RESTORATION OF SUPPLY - Percentage of Interruptions Not Restored within 24 hours
OVERALL RELIABILITY - Number of Faults per 100km of Distribution System (Mains only)
NUMBER OF FAULTS/100KM
Verified Voltage Complaints per 10,000 Connected Customers
COMPLAINTS/10,000 CUSTOMERS
99/00 average
ints/100 custs GB
99/00 average 81 interruptions/100 customers
Mins lost GB
99/00 average 71 mins/cust
Average of faults restored within 24 hours (all companies)
Last year | This year | 99/2000 | 90.55% | 90/91 | 83.6%
99.52% | 99.99% | 98/99 | 89.08% | 91/92 | 88.7%
|  | 97/98 | 89.18% | 92/93 | 87.3%
|  | 96/97 | 88.86% | 93/94 | 87.9%
|  | 95/96 | 87.89% | 94/95 | 88.3%
|  | 90/91 | 83.8% | 95/96 | 88.1%
|  |  |  | 96/97 | 88.8%
Supply Interruptions per 100 Connected Customers | GB 10 year average of averages
LV Faults (All) | 5.7161 | 0% | LV
HV faults:U/G, no dam | 1.4794 | 10% | HV u/g ND
HV faults:U/G, damage | 24.1534 | 10% | HV u/g D
HV faults:O/H, no dam | 7.9419 | 10% | HV o/h ND
HV faults:O/H, damage | 13.8205 | 10% | HV o/h D
HV faults: All other | 15.3463 | 10% | HV other
EHV faults | 11.9719 | 0% | EHV
132kV faults | 5.3277 | 0% | 132kV
(b) Planned Outages | 10.9021 | 0% | Planned
(c) Embedded Gen. | 0.44972 | 0% | Emb. Gen
(d) Other Systems | 1.6885 | 0% | Other
Total of (a+b+c+d) | 99.3973
Sum of averages | 98.7975
DATA FOR TWO PIE CHARTS
Note: "Other" includes generation and transmission
Security 1990/2000 | Number and sources of supply interruptions per 100 customers
LV 10 | 9.9698 | 0% |  | 6
Planned 8 | 8.0708 | 10% |  | 11
HV 58 | 58.0695 | 10% |  | 63
EHV 10 | 10.0456 | 0% |  | 12
132kV 5 | 4.9951 | 0% |  | 5
Other 2 | 1.8562 | 0% |  | 2
Total of (a+b+c+d) | 90.2561 | Average of 93 interruptions per 100 customers |  | 99.3973
Sum of averages | 93.0069 |  |  | 99
Availability 1990/2000 | Number and sources of minutes lost per customer
LV 20 | 20.4564 | 0% |  | 12
Planned 44 | 44.3673 | 10% |  | 25
HV 115 | 115.1228 | 10% |  | 66
EHV 15 | 14.855 | 0% |  | 9
132kV 9 | 8.5745 | 0% |  | 6
Other 1 | 1.2766 | 0% |  | 1
Total of (a+b+c+d) | 206.4288 | Average of 205 minutes per connected customer
Sum of averages | 204.6526
GB circuit lengths (km)
132kV O/H | 15049.1
132kV U/G | 2724
EHV O/H | 28766.8
EHV U/G | 14509.5
HV O/H | 13368.6
HV U/G | 20135.1
LV O/H | 364192.1
LV U/G | 306031.3
km 132kV | 17773.1
km EHV | 43276.3
km HV | 33503.7
km LV | 670223.4
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
inst/100 custs GB | 3481.6984 | 1081.2942 | 1122.5594 | 1301.443 | 1168.428 | 1355.5196 | 1129.4047 | 1058.7337 | 910.1168 | 1050.5405
Mins per cust GB | 181.2859 | 81.6512 | 88.867 | 76.4191 | 79.1788 | 76.6454 | 69.5674 | 71.122 | 66.876 | 55.88
Cust ints GB | 865010531.1439 | 270509993.6154 | 283923651.5523 | 331257667.4742 | 299661562.8607 | 351509767.9491 | 295504453.6821 | 279962128.0484 | 241895382.5714 | 281442315.0752
Cust GB | 24844499 | 25017243 | 25292529 | 25453106 | 25646557 | 25931736 | 26164620 | 26443111 | 26578500 | 26790240
Mins lost GB | 4503956780.28 | 2042687153.58 | 2247670547.42 | 1945102575.11 | 2030663510 | 1987549192.83 | 1820203476.95 | 1880688181 | 1777462720.5 | 1497038148.34

## P
SECURITY TRENDS : Supply Interruptions per 100 Customers
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
SECURITY - ALL PES AVERAGES SINCE VESTING | 123.5877 | 101.2773 | 108.0892 | 96.7121 | 99.6507 | 101.7507 | 95.5493 | 95.0107 | 85.0864 | 87.2586 | average of averages
SECURITY - ALL PES AVERAGES SINCE VESTING | 112.5901 | 88.6026 | 97.0646 | 85.7769 | 89.3689 | 91.9741 | 89.7215 | 88.0105 | 78.2598 | 81.3806 | weighted average
year 1 | 90/91: 27972454.433; 91/92: 24844499; 92/93: 112.5901
2 | 90/91: 22165931.4114; 91/92: 25017243; 92/93: 88.6026
3 | 90/91: 24550085.0954; 91/92: 25292529; 92/93: 97.0646
4 | 90/91: 21832875.7992; 91/92: 25453106; 92/93: 85.7769
5 | 90/91: 22920033.3607; 91/92: 25646557; 92/93: 89.3689
6 | 90/91: 23850473.3491; 91/92: 25931736; 92/93: 91.9741
7 | 90/91: 23475276.8821; 91/92: 26164620; 92/93: 89.7215
8 | 90/91: 23272724.2484; 91/92: 26443111; 92/93: 88.0105
9 | 90/91: 20800276.9714; 91/92: 26578500; 92/93: 78.2598
10 | 90/91: 21802053.9752; 91/92: 26790240; 92/93: 81.3806

## Q
Minutes lost per connected customer
AVAILABILITY TRENDS : Minutes lost per Connected Customers |  | 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
AVAILABILITY - ALL PES AVERAGES SINCE VESTING |  | 229.2936 | 123.6219 | 127.0231 | 111.8029 | 109.9407 | 116.7214 | 97.6243 | 99.5657 | 91.5564 | 76.3843 | average of averages
AVAILABILITY - ALL PES AVERAGES SINCE VESTING |  | 227.4081 | 103.7619 | 107.1533 | 96.1945 | 98.062 | 98.1302 | 87.1743 | 87.765 | 80.7131 | 70.7944 | weighted average
year 1 | 5649840089.08 | 90/91 1: 24844499; 91/92 2: 227.4081
2 | 2595836115.75 | 90/91 1: 25017243; 91/92 2: 103.7619
3 | 2710177846.62 | 90/91 1: 25292529; 91/92 2: 107.1533
4 | 2448449077.61 | 90/91 1: 25453106; 91/92 2: 96.1945
5 | 2514953510 | 90/91 1: 25646557; 91/92 2: 98.062
6 | 2544685452.83 | 90/91 1: 25931736; 91/92 2: 98.1302
7 | 2280882756.95 | 90/91 1: 26164620; 91/92 2: 87.1743
8 | 2320780821 | 90/91 1: 26443111; 91/92 2: 87.765
9 | 2145232360.5 | 90/91 1: 26578500; 91/92 2: 80.7131
10 | 1896599308.34 | 90/91 1: 26790240; 91/92 2: 70.7944
SUMMARY OF PERFORMANCE
Better than 10 yr average:
Security | 12 | 90/91 1: Sec U/G; 91/92 2: 5
Availability | 14 | 90/91 1: Sec O/H; 91/92 2: 10
3hr restn | 13 | 90/91 1: Av U/G; 91/92 2: 8
24hr restn | 14 | 90/91 1: Av O/H; 91/92 2: 13
Voltage | 13
Overall rel | 9
Better than last 9 years
Security | 2 | 90/91 1: Sec U/G; 91/92 2: 1
Availability | 6 | 90/91 1: Sec O/H; 91/92 2: 3
3hr restn | 5 | 90/91 1: Av U/G; 91/92 2: 3
24hr restn | 1 | 90/91 1: Av O/H; 91/92 2: 3
Voltage | 6
Overall rel | 5
3hr and 24 GB summary
Total interruptions in last year
21802053.9752
Total rest in 3 hours
19807419.4471 | 90.85%
Total rest in 24 hours
21800841.9112 | 99.99%