GB SQSS offshore networks review

Cost benefit analysis information

##### Generator

### Availability

96% availability used for onshore turbines a similar number is expected offshore. Source – Windfarm developers.

### ROC value

Assume ROC mechanism does not change – however outcome to be tested against +/- 10, 30 and 50%. Source - DTI

### Constraint costs

£25-33/MWh until 2027, after which it increases to £32-37/MWh. Source – TPCR Third Consultation.

## Wind resource

Weibull parameters c=10, k=2

Predicted Windfarm power output profiles.

Historic wind data to assess Loading capabilities of transformers and cables

##### Offshore substation

Capital Cost to include;

- Foundations

- Installation

- Platform cost

- Increase / decrease in cost for increase / decrease in platform assets and changes in ratings

- Operation and maintenance costs

### Transformers

Reliability

Reliability parameters of different voltages and ratings. We also need to understand more about the drivers behind the values suggested, as these will relate to O&M cost and we need to ensure consistency of our evaluations

Average failure rate of 2% per year for units operating at 700kV and below.

Source: ‘An international survey on failures in large power transformers in service’ – Dated 1983, National Grid’s view that this survey has not been superseded, most reliable information available.

Mean time to repair – 2-10 months

Electrical parameters for as wide a range as possible of offshore transformers

Maintenance requirements

Capital Cost to include;

- Difference in cost  for different ratings / voltages

- Operation and maintenance costs

Cyclic capability. This will be helpful when determining the impact of short term fluctuations of wind power, particularly during outages of circuits.

### LV switchgear

Reliability

Maintenance requirements

Mean time to repair

## Fault level constraints of switchgear

Capital cost

We also need more information on cost of various busbar arrangements to assess the value of flexibility at 33kV and 132kV/220kV for alternative configurations.

### HV switchgear

Reliability

|  | Voltage Class |  |  |
| --- | --- | --- | --- |
|  | 1: 60-100kV | 2: 100-200kV | 4: 300-500kV |
| Total population (failures per 100 CB years) | 0.04 | 0.91 | 2.58 |
| Without Japan (failures per 100 CB years) | 0.18 | 1.37 | 2.58 |
| Circuit-breaker | 36% | 40% | 27% |
| Disconnector | 21% | 17% | 20% |
| Busbars | 14% | 6% | 6% |
| Busducts and interconnecting parts | 7% | 6% | 24% |

Source: ‘Report on the second international survey on high voltage gas insulated substations (GIS) service experience’, CIGRE Ref 150, February 2000, GIS commissioned after 01/01/85.

Fault level constraints of switchgear

Capital cost

We also need more information on cost of various busbar arrangements to assess the value of flexibility at 33kV and 132kV/220kV for alternative configurations.

##### Connection to shore

Cable options

Mean Time to Repair (days)

Failure rate (1/year/100km)

Installation costs (£/m)

Steady state rating (MVA)

Inductance per core (nH/m)

Capacitance per core (pF/m)

Resistance (/m)

Conductor (mm2)

No cores

Voltage (kV)

100

100

100

100

100

100

0.08

0.08

0.08

0.08

0.08

0.08

625

625

343

290

206

174

500

367

399

367

399

100

245

206

245

206

32.5

32.5

32.5

49.3

32.5

49.3

800

800

800

500

800

500

1

1

3

3

3

3

400 DC

400

220

220

132

132

# Members of the sub-group to comment on the values of the parameters

Electrical parameters for as wide a range voltages / ratings of offshore cables.

Cyclic capability. This will be helpful when determining the impact of short term fluctuations of wind power, particularly during outages of circuits.

AC

Maximum ratings

132 kV 	1 x 3-core:  200 MW

3 x 1-core:  300 MW

(figures from www.abb.com)

220 kV

DC

300-500MW modules available 2006

1000MW modules available 2007

Cyclic capability. This will be helpful when determining the impact of short term fluctuations of wind power, particularly during outages of circuits.

Reliability

Reliability parameters of different voltages and ratings. We also need to understand more about the drivers behind the values suggested, as these will relate to O&M cost and we need to ensure consistency of our evaluations

Garrad Hassan & Partners cite CIGRE SC21 1985:  0.32 failures/100 km year, but, in the part of their study addressing the connection to shore, they only use their alternative figure of 0.1 failures/100 km year. Source (www.owen.eru.rl.ac.uk/documents/bwea20_45.pdf)

Grainger and Jenkins cite Wallace and Whittington, 1981:  1.3 failures /100 km year.  Grainger and Jenkins state that this figure is high. Source (www.owen.eru.rl.ac.uk/documents/bwea20_46.pdf)

Time to repair

Mean time to repair  3 months

Capital Cost to include;

- Installation cost.

- Manufacturing Cost per km for various ratings / voltage levels.

- Operation and Maintenance costs.

- Cost of repair

- Increase / decrease in cost for increase / decrease in platform assets and changes in ratings.

- AC and DC solutions.

- Likely cost for technology under development that is likely to be available at the time of installation of these networks.